## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Sensor_Id | Sensor_Type | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV CLOSE STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1334 | Rewari | TK-01_BS VI MS | TK-01 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TK-01 | Primary Radar | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | [8 empty] | MOV.MOV-001.OPEN_STATUS | 1 | MOV-001 | MOV IL1 | MOV.MOV-001.REMOTE_STATUS | 0 | MOV-001 | MOV IL1 |  |  |  |  | MOV.MOV-002.OPEN_STATUS | 1 | MOV-002 | MOV OL | MOV.MOV-002.CLOSE_STATUS | 0 | MOV-002 | MOV OL
1334 | Rewari | TK-02_BS VI MS | TK-02 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TK-02 | Primary Radar | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED OL | [8 empty] | MOV.MOV-004.OPEN_STATUS | 1 | MOV-004 | MOV IL1 | MOV.MOV-004.REMOTE_STATUS | 0 | MOV-004 | MOV IL1 |  |  |  |  | MOV.MOV-005.OPEN_STATUS | 1 | MOV-005 | MOV OL | MOV.MOV-005.CLOSE_STATUS | 0 | MOV-005 | MOV OL
1334 | Rewari | TK-03_ETHANOL | TK-03 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TK-03 | Primary Radar | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED OL | [8 empty] | MOV.MOV-007.OPEN_STATUS | 1 | MOV-007 | MOV IL1 | MOV.MOV-007.REMOTE_STATUS | 0 | MOV-007 | MOV IL1 |  |  |  |  | MOV.MOV-008.OPEN_STATUS | 1 | MOV-008 | MOV OL | MOV.MOV-008.CLOSE_STATUS | 0 | MOV-008 | MOV OL
1334 | Rewari | TK-04_ETHANOL | TK-04 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TK-04 | Primary Radar | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.MOV-010.OPEN_STATUS | 1 | MOV-010 | MOV IL1 | MOV.MOV-010.REMOTE_STATUS | 0 | MOV-010 | MOV IL1 |  |  |  |  | MOV.MOV-011.OPEN_STATUS | 1 | MOV-011 | MOV OL | MOV.MOV-011.CLOSE_STATUS | 0 | MOV-011 | MOV OL
1334 | Rewari | TK-05_ETHANOL | TK-05 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TK-05 | Primary Radar | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL | [8 empty] | MOV.MOV-013.OPEN_STATUS | 1 | MOV-013 | MOV IL1 | MOV.MOV-013.REMOTE_STATUS | 0 | MOV-013 | MOV IL1 |  |  |  |  | MOV.MOV-014.OPEN_STATUS | 1 | MOV-014 | MOV OL | MOV.MOV-014.CLOSE_STATUS | 0 | MOV-014 | MOV OL
1334 | Rewari | TK-06_BS VI HSD | TK-06 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TK-06 | Primary Radar | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar
1334 | Rewari | TK-07_BS VI MS | TK-07 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TK-07 | Primary Radar | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar
1334 | Rewari | TK-08_BS VI HSD | TK-08 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TK-08 | Primary Radar | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1334 | Rewari | TK-09_WATER | TK-09 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  |  |  | TANK.TK-09.TANK_ALERT_ALARM | 0 | TK-09 | Primary Radar
1334 | Rewari | TK-10_WATER | TK-10 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  |  |  | TANK.TK-10.TANK_ALERT_ALARM | 0 | TK-10 | Primary Radar
1334 | Rewari | TK-11_BS VI HSD | TK-11 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.TANK_ALERT_ALARM | 0 | TK-11 | Primary Radar | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED OL | [8 empty] | MOV.MOV-016.OPEN_STATUS | 1 | MOV-016 | MOV IL1 | MOV.MOV-016.REMOTE_STATUS | 0 | MOV-016 | MOV IL1 |  |  |  |  | MOV.MOV-017.OPEN_STATUS | 1 | MOV-017 | MOV OL | MOV.MOV-017.CLOSE_STATUS | 0 | MOV-017 | MOV OL
1334 | Rewari | TK-12_BS VI MS | TK-12 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM | 0 | TK-12 | Primary Radar | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | [8 empty] | MOV.MOV-019.OPEN_STATUS | 1 | MOV-019 | MOV IL1 | MOV.MOV-019.REMOTE_STATUS | 0 | MOV-019 | MOV IL1 |  |  |  |  | MOV.MOV-020.OPEN_STATUS | 1 | MOV-020 | MOV OL | MOV.MOV-020.CLOSE_STATUS | 0 | MOV-020 | MOV OL
1334 | Rewari | TK-13_BS VI HSD | TK-13 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.TANK_ALERT_ALARM | 0 | TK-13 | Primary Radar | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV OL | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED OL | [8 empty] | MOV.MOV-022.OPEN_STATUS | 1 | MOV-022 | MOV IL1 | MOV.MOV-022.REMOTE_STATUS | 0 | MOV-022 | MOV IL1 |  |  |  |  | MOV.MOV-023.OPEN_STATUS | 1 | MOV-023 | MOV OL | MOV.MOV-023.CLOSE_STATUS | 0 | MOV-023 | MOV OL
1334 | Rewari | TK-14_BS VI HSD | TK-14 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TK-14 | Primary Radar | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV IL1 | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV OL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED OL | [8 empty] | MOV.MOV-025.OPEN_STATUS | 1 | MOV-025 | MOV IL1 | MOV.MOV-025.REMOTE_STATUS | 0 | MOV-025 | MOV IL1 |  |  |  |  | MOV.MOV-026.OPEN_STATUS | 1 | MOV-026 | MOV OL | MOV.MOV-026.CLOSE_STATUS | 0 | MOV-026 | MOV OL
1334 | Rewari | TK-15_BS VI MS | TK-15 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | 0 | TK-15 | Primary Radar | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | [8 empty] | MOV.MOV-028.OPEN_STATUS | 1 | MOV-028 | MOV IL1 | MOV.MOV-028.REMOTE_STATUS | 0 | MOV-028 | MOV IL1 |  |  |  |  | MOV.MOV-029.OPEN_STATUS | 1 | MOV-029 | MOV OL | MOV.MOV-029.CLOSE_STATUS | 0 | MOV-029 | MOV OL
1334 | Rewari | TK-16_SLOP | TK-16 |  | SLOP | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar |  |  |  |  | TANK.TK-16.TANK_ALERT_ALARM | 0 | TK-16 | Primary Radar |  |  |  |  | LEVELSWITCH.LSW-11.SWITCH_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_OK | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_FAILED | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.SWITCH_STATUS | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_OK | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_FAILED | 0 | RDR-11 | RADAR | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV IL1 | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV OL | MOV.ROSOV-22.FAILED_TO_CLOSE | 0 | ROSOV-22 | ROSOV FAILED OL | [8 empty] | MOV.MOV-031.OPEN_STATUS | 1 | MOV-031 | MOV IL1 | MOV.MOV-031.REMOTE_STATUS | 0 | MOV-031 | MOV IL1 |  |  |  |  | MOV.MOV-032.OPEN_STATUS | 1 | MOV-032 | MOV OL | MOV.MOV-032.CLOSE_STATUS | 0 | MOV-032 | MOV OL | MOV.MOV-033.OPEN_STATUS |  | MOV-033 | MOV RCL | MOV.MOV-033.REMOTE_STATUS | 0 | MOV-033 | MOV RCL
1334 | Rewari | TK-17_SLOP | TK-17 |  | SLOP | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar |  |  |  |  | TANK.TK-17.TANK_ALERT_ALARM | 0 | TK-17 | Primary Radar |  |  |  |  | LEVELSWITCH.LSW-12.SWITCH_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_OK | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_FAILED | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.SWITCH_STATUS | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_OK | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_FAILED | 0 | RDR-12 | RADAR | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV IL1 | MOV.ROSOV-23.FAILED_TO_CLOSE | 0 | ROSOV-23 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV OL | MOV.ROSOV-24.FAILED_TO_CLOSE | 0 | ROSOV-24 | ROSOV FAILED OL | [8 empty] | MOV.MOV-034.OPEN_STATUS | 1 | MOV-034 | MOV IL1 | MOV.MOV-034.REMOTE_STATUS | 0 | MOV-034 | MOV IL1 |  |  |  |  | MOV.MOV-035.OPEN_STATUS | 1 | MOV-035 | MOV OL | MOV.MOV-035.CLOSE_STATUS | 0 | MOV-035 | MOV OL
1334 | Rewari | TK-18_ETHANOL | TK-18 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-18.LEVEL |  | TK-18 | Primary Radar | TANK.TK-18.HIGH_LEVEL | 0 | TK-18 | Primary Radar | TANK.TK-18.TANK_ALERT_ALARM | 0 | TK-18 | Primary Radar | TANK.TK-18.HIGH_HIGH_LEVEL | 0 | TK-18 | Primary Radar
1334 | Rewari | TK-19_ETHANOL | TK-19 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-19.LEVEL |  | TK-19 | Primary Radar | TANK.TK-19.HIGH_LEVEL | 0 | TK-19 | Primary Radar | TANK.TK-19.TANK_ALERT_ALARM | 0 | TK-19 | Primary Radar | TANK.TK-19.HIGH_HIGH_LEVEL | 0 | TK-19 | Primary Radar
1334 | Rewari | TK-20_ETHANOL | TK-20 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-20.LEVEL |  | TK-20 | Primary Radar | TANK.TK-20.HIGH_LEVEL | 0 | TK-20 | Primary Radar | TANK.TK-20.TANK_ALERT_ALARM | 0 | TK-20 | Primary Radar | TANK.TK-20.HIGH_HIGH_LEVEL | 0 | TK-20 | Primary Radar
1334 | Rewari | TK-21_ETHANOL | TK-21 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-21.LEVEL |  | TK-21 | Primary Radar | TANK.TK-21.HIGH_LEVEL | 0 | TK-21 | Primary Radar | TANK.TK-21.TANK_ALERT_ALARM | 0 | TK-21 | Primary Radar | TANK.TK-21.HIGH_HIGH_LEVEL | 0 | TK-21 | Primary Radar
1334 | Rewari | TK-26_BS VI MS | TK-26 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-26.LEVEL |  | TK-26 | Primary Radar | TANK.TK-26.HIGH_LEVEL | 0 | TK-26 | Primary Radar | TANK.TK-26.TANK_ALERT_ALARM | 0 | TK-26 | Primary Radar | TANK.TK-26.HIGH_HIGH_LEVEL | 0 | TK-26 | Primary Radar | LEVELSWITCH.LSW-13.SWITCH_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_OK | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_FAILED | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.SWITCH_STATUS | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_OK | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_FAILED | 0 | RDR-13 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | 0 | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-26.OPEN_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | 0 | ROSOV-26 | ROSOV FAILED OL | [8 empty] | MOV.MOV-037.OPEN_STATUS | 1 | MOV-037 | MOV IL1 | MOV.MOV-037.REMOTE_STATUS | 0 | MOV-037 | MOV IL1 |  |  |  |  | MOV.MOV-038.OPEN_STATUS | 1 | MOV-038 | MOV OL | MOV.MOV-038.CLOSE_STATUS | 0 | MOV-038 | MOV OL
1334 | Rewari | TK-27_BS VI HSD | TK-27 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-27.LEVEL |  | TK-27 | Primary Radar | TANK.TK-27.HIGH_LEVEL | 0 | TK-27 | Primary Radar | TANK.TK-27.TANK_ALERT_ALARM | 0 | TK-27 | Primary Radar | TANK.TK-27.HIGH_HIGH_LEVEL | 0 | TK-27 | Primary Radar | LEVELSWITCH.LSW-14.SWITCH_STATUS | 0 | LSW-14 | VFT | LEVELSWITCH.LSW-14.PROOF_TEST_OK | 0 | LSW-14 | VFT | LEVELSWITCH.LSW-14.PROOF_TEST_FAILED | 0 | LSW-14 | VFT | LEVELSWITCH.RDR-14.SWITCH_STATUS | 0 | RDR-14 | RADAR | LEVELSWITCH.RDR-14.PROOF_TEST_OK | 0 | RDR-14 | RADAR | LEVELSWITCH.RDR-14.PROOF_TEST_FAILED | 0 | RDR-14 | RADAR | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV IL1 | MOV.ROSOV-27.FAILED_TO_CLOSE | 0 | ROSOV-27 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-28.OPEN_STATUS | 0 | ROSOV-28 | ROSOV OL | MOV.ROSOV-28.FAILED_TO_CLOSE | 0 | ROSOV-28 | ROSOV FAILED OL | [8 empty] | MOV.MOV-040.OPEN_STATUS | 1 | MOV-040 | MOV IL1 | MOV.MOV-040.REMOTE_STATUS | 0 | MOV-040 | MOV IL1 |  |  |  |  | MOV.MOV-041.OPEN_STATUS | 1 | MOV-041 | MOV OL | MOV.MOV-041.CLOSE_STATUS | 0 | MOV-041 | MOV OL
1334 | Rewari | TK-28_BS VI HSD | TK-28 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-28.LEVEL |  | TK-28 | Primary Radar | TANK.TK-28.HIGH_LEVEL | 0 | TK-28 | Primary Radar | TANK.TK-28.TANK_ALERT_ALARM | 0 | TK-28 | Primary Radar | TANK.TK-28.HIGH_HIGH_LEVEL | 0 | TK-28 | Primary Radar | LEVELSWITCH.LSW-15.SWITCH_STATUS | 0 | LSW-15 | VFT | LEVELSWITCH.LSW-15.PROOF_TEST_OK | 0 | LSW-15 | VFT | LEVELSWITCH.LSW-15.PROOF_TEST_FAILED | 0 | LSW-15 | VFT | LEVELSWITCH.RDR-15.SWITCH_STATUS | 0 | RDR-15 | RADAR | LEVELSWITCH.RDR-15.PROOF_TEST_OK | 0 | RDR-15 | RADAR | LEVELSWITCH.RDR-15.PROOF_TEST_FAILED | 0 | RDR-15 | RADAR | MOV.ROSOV-29.OPEN_STATUS | 0 | ROSOV-29 | ROSOV IL1 | MOV.ROSOV-29.FAILED_TO_CLOSE | 0 | ROSOV-29 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-30.OPEN_STATUS | 0 | ROSOV-30 | ROSOV OL | MOV.ROSOV-30.FAILED_TO_CLOSE | 0 | ROSOV-30 | ROSOV FAILED OL | [8 empty] | MOV.MOV-043.OPEN_STATUS | 1 | MOV-043 | MOV IL1 | MOV.MOV-043.REMOTE_STATUS | 0 | MOV-043 | MOV IL1 |  |  |  |  | MOV.MOV-044.OPEN_STATUS | 1 | MOV-044 | MOV OL | MOV.MOV-044.CLOSE_STATUS | 0 | MOV-044 | MOV OL
1334 | Rewari | TK-29_WATER | TK-29 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-29.LEVEL |  | TK-29 | Primary Radar |  |  |  |  | TANK.TK-29.TANK_ALERT_ALARM | 0 | TK-29 | Primary Radar
1334 | Rewari | TK-30_WATER | TK-30 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-30.LEVEL |  | TK-30 | Primary Radar |  |  |  |  | TANK.TK-30.TANK_ALERT_ALARM | 0 | TK-30 | Primary Radar
1334 | Rewari | TK-32_ETHANOL | TK-32 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | [6 empty] | TANK.TK-32.LEVEL |  | TK-32 | Primary Radar | TANK.TK-32.HIGH_LEVEL | 0 | TK-32 | Primary Radar | TANK.TK-32.TANK_ALERT_ALARM | 0 | TK-32 | Primary Radar | TANK.TK-32.HIGH_HIGH_LEVEL | 0 | TK-32 | Primary Radar

## HDR Line MOV
SAPID | Location | Device Name | Product | MOV ID | HDR MOV STATUS | Normal Value | HDR MOV REMOTE STATUS | Normal Value | HDR MOV MAINTENANCE STATUS | Normal Value
1334 | Rewari | MOV-PPL-HSD1_HSD1 | HSD1 | MOV-PPL-HSD1 | MOV.MOV-PPL-HSD1.OPEN_STATUS | TRUE
1334 | Rewari | MOV-PPL-HSD2_HSD2 | HSD2 | MOV-PPL-HSD2 | MOV.MOV-PPL-HSD2.OPEN_STATUS | TRUE
1334 | Rewari | MOV-PPL-MS1_MS1 | MS1 | MOV-PPL-MS1 | MOV.MOV-PPL-MS1.OPEN_STATUS | TRUE
1334 | Rewari | MOV-PPL-MS2_MS2 | MS2 | MOV-PPL-MS2 | MOV.MOV-PPL-MS2.OPEN_STATUS | TRUE
1334 | Rewari | MOV-PPL-SLOP_SLOP | SLOP | MOV-PPL-SLOP | MOV.MOV-PPL-SLOP.OPEN_STATUS | TRUE
1334 | Rewari | TOBV-003_BS VI MS | BS VI MS | TOBV-003 | MOV.TOBV-003.OPEN_STATUS | TRUE | MOV.TOBV-003.REMOTE_STATUS | TRUE | MOV.TOBV-003.MAINTENANCE_STATUS | TRUE
1334 | Rewari | TOBV-004_BS VI HSD | BS VI HSD | TOBV-004 | MOV.TOBV-004.OPEN_STATUS | TRUE | MOV.TOBV-004.REMOTE_STATUS | TRUE | MOV.TOBV-004.MAINTENANCE_STATUS | TRUE
1334 | Rewari | TOBV-001_ETHANOL | ETHANOL | TOBV-001 | MOV.TOBV-001.OPEN_STATUS | TRUE | MOV.TOBV-001.REMOTE_STATUS | TRUE | MOV.TOBV-001.MAINTENANCE_STATUS | TRUE
1334 | Rewari | TOBV-002_BIOHSD | BIOHSD | TOBV-002 | MOV.TOBV-002.OPEN_STATUS | TRUE | MOV.TOBV-002.REMOTE_STATUS | TRUE | MOV.TOBV-002.MAINTENANCE_STATUS | TRUE

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value | Sensor_id | Sensor_Type
1334 | Rewari_M | TK-01_BS VI MS | TK-01 |  | BS VI MS | TANK.TK-01.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | [16 empty] | MOV.MOV-001.MAINTENANCE_STATUS | 0 | MOV-001 | MOV IL1
1334 | Rewari_M | TK-02_BS VI MS | TK-02 |  | BS VI MS | TANK.TK-02.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | [16 empty] | MOV.MOV-004.MAINTENANCE_STATUS | 0 | MOV-004 | MOV IL1
1334 | Rewari_M | TK-03_ETHANOL | TK-03 |  | ETHANOL | TANK.TK-03.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | [16 empty] | MOV.MOV-007.MAINTENANCE_STATUS | 0 | MOV-007 | MOV IL1
1334 | Rewari_M | TK-04_ETHANOL | TK-04 |  | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | [16 empty] | MOV.MOV-010.MAINTENANCE_STATUS | 0 | MOV-010 | MOV IL1
1334 | Rewari_M | TK-05_ETHANOL | TK-05 |  | ETHANOL | TANK.TK-05.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | [16 empty] | MOV.MOV-013.MAINTENANCE_STATUS | 0 | MOV-013 | MOV IL1
1334 | Rewari_M | TK-06_BS VI HSD | TK-06 |  | BS VI HSD | TANK.TK-06.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-07_BS VI MS | TK-07 |  | BS VI MS | TANK.TK-07.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-08_BS VI HSD | TK-08 |  | BS VI HSD | TANK.TK-08.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-09_WATER | TK-09 |  | WATER
1334 | Rewari_M | TK-10_WATER | TK-10 |  | WATER
1334 | Rewari_M | TK-11_BS VI HSD | TK-11 |  | BS VI HSD | TANK.TK-11.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | [16 empty] | MOV.MOV-016.MAINTENANCE_STATUS | 0 | MOV-016 | MOV IL1
1334 | Rewari_M | TK-12_BS VI MS | TK-12 |  | BS VI MS | TANK.TK-12.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | [16 empty] | MOV.MOV-019.MAINTENANCE_STATUS | 0 | MOV-019 | MOV IL1
1334 | Rewari_M | TK-13_BS VI HSD | TK-13 |  | BS VI HSD | TANK.TK-13.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | [16 empty] | MOV.MOV-022.MAINTENANCE_STATUS | 0 | MOV-022 | MOV IL1
1334 | Rewari_M | TK-14_BS VI HSD | TK-14 |  | BS VI HSD | TANK.TK-14.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | [16 empty] | MOV.MOV-025.MAINTENANCE_STATUS | 0 | MOV-025 | MOV IL1
1334 | Rewari_M | TK-15_BS VI MS | TK-15 |  | BS VI MS | TANK.TK-15.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | [16 empty] | MOV.MOV-028.MAINTENANCE_STATUS | 0 | MOV-028 | MOV IL1
1334 | Rewari_M | TK-16_SLOP | TK-16 |  | SLOP |  |  |  |  | LEVELSWITCH.LSW-11.MAINTENANCE_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.MAINTENANCE_STATUS | 0 | RDR-11 | RADAR | [16 empty] | MOV.MOV-031.MAINTENANCE_STATUS | 0 | MOV-031 | MOV IL1 |  |  |  |  | MOV.MOV-033.MAINTENANCE_STATUS | 0 | MOV-033 | MOV RCL
1334 | Rewari_M | TK-17_SLOP | TK-17 |  | SLOP |  |  |  |  | LEVELSWITCH.LSW-12.MAINTENANCE_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.MAINTENANCE_STATUS | 0 | RDR-12 | RADAR | [16 empty] | MOV.MOV-034.MAINTENANCE_STATUS | 0 | MOV-034 | MOV IL1
1334 | Rewari_M | TK-18_ETHANOL | TK-18 |  | ETHANOL | TANK.TK-18.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-19_ETHANOL | TK-19 |  | ETHANOL | TANK.TK-19.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-20_ETHANOL | TK-20 |  | ETHANOL | TANK.TK-20.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-21_ETHANOL | TK-21 |  | ETHANOL | TANK.TK-21.MAINTENANCE_STATUS | 0
1334 | Rewari_M | TK-26_BS VI MS | TK-26 |  | BS VI MS | TANK.TK-26.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-13.MAINTENANCE_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.MAINTENANCE_STATUS | 0 | RDR-13 | RADAR | [16 empty] | MOV.MOV-037.MAINTENANCE_STATUS |  | MOV-037 | MOV IL1
1334 | Rewari_M | TK-27_BS VI HSD | TK-27 |  | BS VI HSD | TANK.TK-27.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-14.MAINTENANCE_STATUS | 0 | LSW-14 | VFT | LEVELSWITCH.RDR-14.MAINTENANCE_STATUS | 0 | RDR-14 | RADAR | [16 empty] | MOV.MOV-040.MAINTENANCE_STATUS |  | MOV-040 | MOV IL1
1334 | Rewari_M | TK-28_BS VI HSD | TK-28 |  | BS VI HSD | TANK.TK-28.MAINTENANCE_STATUS | 0 |  |  | LEVELSWITCH.LSW-15.MAINTENANCE_STATUS | 0 | LSW-15 | VFT | LEVELSWITCH.RDR-15.MAINTENANCE_STATUS | 0 | RDR-15 | RADAR | [16 empty] | MOV.MOV-043.MAINTENANCE_STATUS | 0 | MOV-043 | MOV IL1
1334 | Rewari_M | TK-29_WATER | TK-29 |  | WATER
1334 | Rewari_M | TK-30_WATER | TK-30 |  | WATER
1334 | Rewari_M | TK-32_ETHANOL | TK-32 |  | ETHANOL | TANK.TK-32.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | Sensor_Id | Sensor_Type | PUMP OFF STATUS | PUMP OFF STATUS Normal value | Sensor_Id | Sensor_Type | PUMP LR STATUS | PUMP LR STATUS Normal value | Sensor_Id | Sensor_Type | PUMP MAINTENANCE STATUS | Normal Value | Sensor_Id | Sensor_Type
1334 | Rewari | ADTV-PMP-01_POWERMS | ADTV-PMP-01 | POWERMS | Truck Loading |  | PUMP.ADTV-PMP-01.ON | 1 |  |  | PUMP.ADTV-PMP-01.OFF | 0 |  |  | PUMP.ADTV-PMP-01.LOCAL_STATUS | 0 |  |  | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1334 | Rewari | ADTV-PMP-02_POWERMS | ADTV-PMP-02 | POWERMS | Truck Loading |  | PUMP.ADTV-PMP-02.ON | 1 |  |  | PUMP.ADTV-PMP-02.OFF | 0 |  |  | PUMP.ADTV-PMP-02.LOCAL_STATUS | 0 |  |  | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1334 | Rewari | ADTV-PMP-03_TURBOHSD | ADTV-PMP-03 | TURBOHSD | Truck Loading |  | PUMP.ADTV-PMP-03.ON | 1 |  |  | PUMP.ADTV-PMP-03.OFF | 0 |  |  | PUMP.ADTV-PMP-03.LOCAL_STATUS | 0 |  |  | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1334 | Rewari | ADTV-PMP-04_TURBOHSD | ADTV-PMP-04 | TURBOHSD | Truck Loading |  | PUMP.ADTV-PMP-04.ON | 1 |  |  | PUMP.ADTV-PMP-04.OFF | 0 |  |  | PUMP.ADTV-PMP-04.LOCAL_STATUS | 0 |  |  | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-01_ETHANOL | PMP-01 | ETHANOL | Truck Loading |  | PUMP.PMP-01.ON | 1 |  |  | PUMP.PMP-01.OFF | 0 |  |  | PUMP.PMP-01.LOCAL_STATUS | 0 |  |  | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-02_ETHANOL | PMP-02 | ETHANOL | Truck Loading |  | PUMP.PMP-02.ON | 1 |  |  | PUMP.PMP-02.OFF | 0 |  |  | PUMP.PMP-02.LOCAL_STATUS | 0 |  |  | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-03_ETHANOL | PMP-03 | ETHANOL | Truck Loading |  | PUMP.PMP-03.ON | 1 |  |  | PUMP.PMP-03.OFF | 0 |  |  | PUMP.PMP-03.LOCAL_STATUS | 0 |  |  | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-04_WATER | PMP-04 | WATER | Truck Loading |  | PUMP.PMP-04.ON | 1 |  |  | PUMP.PMP-04.OFF | 0 |  |  | PUMP.PMP-04.LOCAL_STATUS | 0 |  |  | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-05_WATER | PMP-05 | WATER | Truck Loading |  | PUMP.PMP-05.ON | 1 |  |  | PUMP.PMP-05.OFF | 0 |  |  | PUMP.PMP-05.LOCAL_STATUS | 0 |  |  | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-06_BS VI MS | PMP-06 | BS VI MS | Truck Loading |  | PUMP.PMP-06.ON | 1 |  |  | PUMP.PMP-06.OFF | 0 |  |  | PUMP.PMP-06.LOCAL_STATUS | 0 |  |  | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-07_BS VI MS | PMP-07 | BS VI MS | Truck Loading |  | PUMP.PMP-07.ON | 1 |  |  | PUMP.PMP-07.OFF | 0 |  |  | PUMP.PMP-07.LOCAL_STATUS | 0 |  |  | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-08_BS VI MS | PMP-08 | BS VI MS | Truck Loading |  | PUMP.PMP-08.ON | 1 |  |  | PUMP.PMP-08.OFF | 0 |  |  | PUMP.PMP-08.LOCAL_STATUS | 0 |  |  | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-09_BS VI HSD | PMP-09 | BS VI HSD | Truck Loading |  | PUMP.PMP-09.ON | 1 |  |  | PUMP.PMP-09.OFF | 0 |  |  | PUMP.PMP-09.LOCAL_STATUS | 0 |  |  | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-10_BS VI HSD | PMP-10 | BS VI HSD | Truck Loading |  | PUMP.PMP-10.ON | 1 |  |  | PUMP.PMP-10.OFF | 0 |  |  | PUMP.PMP-10.LOCAL_STATUS | 0 |  |  | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-11_BS VI HSD | PMP-11 | BS VI HSD | Truck Loading |  | PUMP.PMP-11.ON | 1 |  |  | PUMP.PMP-11.OFF | 0 |  |  | PUMP.PMP-11.LOCAL_STATUS | 0 |  |  | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-12_BS VI HSD | PMP-12 | BS VI HSD | Truck Loading |  | PUMP.PMP-12.ON | 1 |  |  | PUMP.PMP-12.OFF | 0 |  |  | PUMP.PMP-12.LOCAL_STATUS | 0 |  |  | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-13_BS VI HSD | PMP-13 | BS VI HSD | Truck Loading |  | PUMP.PMP-13.ON | 1 |  |  | PUMP.PMP-13.OFF | 0 |  |  | PUMP.PMP-13.LOCAL_STATUS | 0 |  |  | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-18_ETHANOL | PMP-18 | ETHANOL | Truck Loading |  | PUMP.PMP-18.ON | 1 |  |  | PUMP.PMP-18.OFF | 0 |  |  | PUMP.PMP-18.LOCAL_STATUS | 0 |  |  | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-19_ETHANOL | PMP-19 | ETHANOL | Truck Loading |  | PUMP.PMP-19.ON | 1 |  |  | PUMP.PMP-19.OFF | 0 |  |  | PUMP.PMP-19.LOCAL_STATUS | 0 |  |  | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-20_ETHANOL | PMP-20 | ETHANOL | Truck Loading |  | PUMP.PMP-20.ON | 1 |  |  | PUMP.PMP-20.OFF | 0 |  |  | PUMP.PMP-20.LOCAL_STATUS | 0 |  |  | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-21_ETHANOL | PMP-21 | ETHANOL | Truck Loading |  | PUMP.PMP-21.ON | 1 |  |  | PUMP.PMP-21.OFF | 0 |  |  | PUMP.PMP-21.LOCAL_STATUS | 0 |  |  | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-22_ETHANOL | PMP-22 | ETHANOL | Truck Loading |  | PUMP.PMP-22.ON | 1 |  |  | PUMP.PMP-22.OFF | 0 |  |  | PUMP.PMP-22.LOCAL_STATUS | 0 |  |  | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1334 | Rewari | PMP-IOCL-01_BS VI MS | PMP-IOCL-01 | BS VI MS | Wagon Loading |  | PUMP.PMP-IOCL-01.ON | 1 |  |  | PUMP.PMP-IOCL-01.OFF | 0
1334 | Rewari | PMP-IOCL-02_BS VI MS | PMP-IOCL-02 | BS VI MS | Wagon Loading |  | PUMP.PMP-IOCL-02.ON | 1 |  |  | PUMP.PMP-IOCL-02.OFF | 0
1334 | Rewari | PMP-IOCL-03_BS VI HSD | PMP-IOCL-03 | BS VI HSD | Wagon Loading |  | PUMP.PMP-IOCL-03.ON | 1 |  |  | PUMP.PMP-IOCL-03.OFF | 0
1334 | Rewari | PMP-IOCL-04_BS VI HSD | PMP-IOCL-04 | BS VI HSD | Wagon Loading |  | PUMP.PMP-IOCL-04.ON | 1 |  |  | PUMP.PMP-IOCL-04.OFF | 0
1334 | Rewari | PMP-IOCL-05_BS VI HSD | PMP-IOCL-05 | BS VI HSD | Wagon Loading |  | PUMP.PMP-IOCL-05.ON | 1 |  |  | PUMP.PMP-IOCL-05.OFF | 0
1334 | Rewari | PMP-IOCL-06_BS VI HSD | PMP-IOCL-06 | BS VI HSD | Wagon Loading |  | PUMP.PMP-IOCL-06.ON | 1 |  |  | PUMP.PMP-IOCL-06.OFF | 0
1334 | Rewari | PMP-IOCL-07_BS VI HSD | PMP-IOCL-07 | BS VI HSD | Wagon Loading |  | PUMP.PMP-IOCL-07.ON | 1 |  |  | PUMP.PMP-IOCL-07.OFF | 0
1334 | Rewari | VRU-PMP-01_BS IV HSD | VRU-PMP-01 | BS IV HSD | Both |  | PUMP.VRU-PMP-01.ON | 1 |  |  | PUMP.VRU-PMP-01.OFF | 0 | [6 empty] | PUMP.VRU-PMP-01.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | Sensor_Id | Sensor_Type | PUMP OFF STATUS | PUMP OFF STATUS Normal value | Sensor_Id | Sensor_Type | PUMP LR STATUS | PUMP LR STATUS Normal value | Sensor_Id | Sensor_Type | FIRE PUMP MAINTENANCE | FIRE PUMP MAINTENANCE Normal value | Sensor_Id | Sensor_Type | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | Sensor_Id | Sensor_Type | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | Sensor_Id | Sensor_Type | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | Sensor_Id | Sensor_Type | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | Sensor_Id | Sensor_Type | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | Sensor_Id | Sensor_Type | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | Sensor_Id | Sensor_Type | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | FWP-01_Water_DISPATCH | FWP-01 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-01.ON | 1 |  |  | PUMP.FWP-01.OFF | 0 |  |  | PUMP.FWP-01.LOCAL_STATUS | 0 | [26 empty] | PUMP.FWP-01.LOW_LUBE_OIL_PRESSURE_ALARM | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1334 | Rewari | FWP-02_Water_DISPATCH | FWP-02 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-02.ON | 1 |  |  | PUMP.FWP-02.OFF | 0 |  |  | PUMP.FWP-02.LOCAL_STATUS | 0 | [26 empty] | PUMP.FWP-02.LOW_LUBE_OIL_PRESSURE_ALARM | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1334 | Rewari | FWP-03_Water_DISPATCH | FWP-03 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-03.ON | 1 |  |  | PUMP.FWP-03.OFF | 0 |  |  | PUMP.FWP-03.LOCAL_STATUS | 0 | [26 empty] | PUMP.FWP-03.LOW_LUBE_OIL_PRESSURE_ALARM | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1334 | Rewari | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-01.ON | 1 |  |  | PUMP.JCY-01.OFF | 0 |  |  | PUMP.JCY-01.LOCAL_STATUS | 0 | [22 empty] | PUMP.JCY-01.PUMP_TRIPPED | 0
1334 | Rewari | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-02.ON | 1 |  |  | PUMP.JCY-02.OFF | 0 |  |  | PUMP.JCY-02.LOCAL_STATUS | 0 | [22 empty] | PUMP.JCY-02.PUMP_TRIPPED | 0
1334 | Rewari | FARTHEST_POINT_PT | FARTHEST | POINT |  | PT | [12 empty] | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0
1334 | Rewari | NEAREST_POINT_PT | NEAREST | POINT |  | PT | [12 empty] | PressureTransmitter.PT-03.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | Sensor_Id | Sensor_Type | LOW BATTERY | LOW BATTERY Normal Value | Sensor_Id | Sensor_Type | UPS ON | UPS ON Normal Value | Sensor_Id | Sensor_Type | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value | Sensor_Id | Sensor_Type
1334 | Rewari | UPS-01_Control Room | UPS-01 | Control Room | UPS.UPS-01.MAIN_AC_FAIL | 0 |  |  | UPS.UPS-01.LOW_BATTERY | 0 |  |  | UPS.UPS-01.LOAD_ON_UPS | 0
1334 | Rewari | UPS-02_Control Room | UPS-02 | Control Room | UPS.UPS-02.MAIN_AC_FAIL | 0 |  |  | UPS.UPS-02.LOW_BATTERY | 0 |  |  | UPS.UPS-02.LOAD_ON_UPS | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | PLC A IS MASTER Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | PLC B IS MASTER Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | PLC A FAIL SAFE Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | PLC B FAIL SAFE Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | PLC A COOMUNCIATION Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | PLC B COOMUNCIATION Normal Value | Sensor_Id | Sensor_Type
1334 | Rewari | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLC A | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLC B
1334 | Rewari | SFT PLC_Safety PLC | SFT PLC | Safety PLC

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | Sensor_Id | Sensor_Type | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | Sensor_Id | Sensor_Type | HCD FAULT | HCD FAULT Normal Value | Sensor_Id | Sensor_Type | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | Sensor_Id | Sensor_Type | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | Sensor_Id | Sensor_Type | HCD Hooter Activated | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | HDS-01_OP-HCD-AT-PUMPHOUSE_OPEN TYPE AT PUMP HOUSE 1 | HDS-01 | OP-HCD-AT-PUMPHOUSE | OPEN TYPE AT PUMP HOUSE 1 | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-01.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-02_OP-HCD-NEAR-TK1-2_OPEN TYPE AT MS DYKE1 NEAR TK1-2 | HDS-02 | OP-HCD-NEAR-TK1-2 | OPEN TYPE AT MS DYKE1 NEAR TK1-2 | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-02.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-03_OP-HCD-NEAR-TK16-17_OPEN TYPE AT MS DYKE1 NEAR TK16-17 | HDS-03 | OP-HCD-NEAR-TK16-17 | OPEN TYPE AT MS DYKE1 NEAR TK16-17 | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-03.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-04_OP-HCD-NEAR-TK15_OPEN TYPE AT MS DYKE 2 NEAR TK15 | HDS-04 | OP-HCD-NEAR-TK15 | OPEN TYPE AT MS DYKE 2 NEAR TK15 | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-04.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-05_P-HCD-NEAR-TK17_FIXED HCD AT MS DYKE4 NEAR TK17 | HDS-05 | P-HCD-NEAR-TK17 | FIXED HCD AT MS DYKE4 NEAR TK17 | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-05.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-06_OP-HCD-NEAR-TK12-26_OPEN TYPE NEAR AT MS DYKE1 NEAR TK12-26 | HDS-06 | OP-HCD-NEAR-TK12-26 | OPEN TYPE NEAR AT MS DYKE1 NEAR TK12-26 | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-06.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-07_P-HCD-NEAR-TK26_FIXED TYPE MS DYKE1 NEAR TK26 | HDS-07 | P-HCD-NEAR-TK26 | FIXED TYPE MS DYKE1 NEAR TK26 | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-07.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-08_P-HDS-AT-PH-DRAIN_FIXED TYPE AT PUMP HOUSE DRAIN | HDS-08 | P-HDS-AT-PH-DRAIN | FIXED TYPE AT PUMP HOUSE DRAIN | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-08.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HDS-09_NEAR_TK-04_NEAR_TK-04 | HDS-09 | NEAR_TK-04 | NEAR_TK-04 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 |  |  | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 |  |  | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 |  |  | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 |  |  | GDS.HDS-09.MAINTENANCE_CALL | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-05 | DRAINVALVE.DV-05.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-06 | DRAINVALVE.DV-06.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-07 | DRAINVALVE.DV-07.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1334 | Rewari | DV-08 | DRAINVALVE.DV-08.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | Sensor_Id | Sensor_Type | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | Sensor_Id | Sensor_Type | BARRIER GATE LR STATUS | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 |  |  | GATE.EntryGate.CLOSE_STATUS | 0 |  |  | GATE.EntryGate.REMOTE_STATUS | 1
1334 | Rewari | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 |  |  | GATE.ExitGate.CLOSE_STATUS | 0 |  |  | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value | Sensor_Id | Sensor_Type
1334 | Rewari | HOOTER_FIELD_1_Dedicated Hooter cum strobe for TLF P/H Activated in Field | HOOTER_FIELD_1 | Dedicated Hooter cum strobe for TLF P/H Activated in Field | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1334 | Rewari | HOOTER_FIELD_2_Dedicated Hooter cum strobe for Near TK-01 Activated in Field | HOOTER_FIELD_2 | Dedicated Hooter cum strobe for Near TK-01 Activated in Field | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1334 | Rewari | HOOTER_FIELD_3_Dedicated Hooter cum strobe for Near TK-12 Activated in Field | HOOTER_FIELD_3 | Dedicated Hooter cum strobe for Near TK-12 Activated in Field | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1334 | Rewari | HOOTER_FIELD_4_Dedicated Hooter cum strobe for Near TK-15 Activated in Field | HOOTER_FIELD_4 | Dedicated Hooter cum strobe for Near TK-15 Activated in Field | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1334 | Rewari | HOOTER_FIELD_5_Dedicated Hooter cum strobe for Near TK-16 Activated in Field | HOOTER_FIELD_5 | Dedicated Hooter cum strobe for Near TK-16 Activated in Field | PLC.SFTPLC.HOOTER_FIELD_5 | 0
1334 | Rewari | HOOTER_FOR_ESD_CR_Dedicated Hooter cum strobe for ESD activated in control room | HOOTER_FOR_ESD_CR | Dedicated Hooter cum strobe for ESD activated in control room | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1334 | Rewari | HOOTER_FOR_HC_CR_Dedicated Hooter cum strobe for HC detector activated in control room | HOOTER_FOR_HC_CR | Dedicated Hooter cum strobe for HC detector activated in control room | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1334 | Rewari | HOOTER_FOR_RIMSEAL_CR_Dedicated Hooter cum strobe for FAP/Dyke activated in control room | HOOTER_FOR_RIMSEAL_CR | Dedicated Hooter cum strobe for FAP/Dyke activated in control room | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | Sensor_Id | Sensor_Type | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | Sensor_Id | Sensor_Type | All ROSOVs closed | Normal value | Sensor_Id | Sensor_Type | Barrier Gate opened | Normal Value | Sensor_Id | Sensor_Type | TLF Gantry Permissive Power Off | Normal value | Sensor_Id | Sensor_Type | All TLF Product Pumps Stopped | Normal value | Sensor_Id | Sensor_Type | All Tanks in Dormant Mode | Normal value | Sensor_Id | Sensor_Type | All DBBVs Closed | Normal value | Sensor_Id | Sensor_Type | ESD Command To Process PLC | Normal value | Sensor_Id | Sensor_Type | Siren Activated | Normal value | Sensor_Id | Sensor_Type | ESD Hooter activated in control room | Normal value | Sensor_Id | Sensor_Type | Power ESD Activation after 120 Sec | Normal value | Sensor_Id | Sensor_Type | TTL Dispatch in Dormant Mode | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | ESD-01_ESD AT GANTRY SUPERVISOR CABIN | ESD-01 | ESD-01 | ESD AT GANTRY SUPERVISOR CABIN | ESD.ESD-01.ESD_STATUS | 0 |  |  | ESD.ESD-01.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-02_ESD AT CONTROL ROOM | ESD-02 | ESD-02 | ESD AT CONTROL ROOM | ESD.ESD-02.ESD_STATUS | 0 |  |  | ESD.ESD-02.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-03_ESD AT INSIDE PRODUCT PUMP HOUSE | ESD-03 | ESD-03 | ESD AT INSIDE PRODUCT PUMP HOUSE | ESD.ESD-03.ESD_STATUS | 0 |  |  | ESD.ESD-03.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-04_ESD AT SECURITY MAIN GATE | ESD-04 | ESD-04 | ESD AT SECURITY MAIN GATE | ESD.ESD-04.ESD_STATUS | 0 |  |  | ESD.ESD-04.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-05_ESD AT BEHIND BAY-08 | ESD-05 | ESD-05 | ESD AT BEHIND BAY-08 | ESD.ESD-05.ESD_STATUS | 0 |  |  | ESD.ESD-05.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-06_ESD AT IN FRONT OF PUMP HOUSE | ESD-06 | ESD-06 | ESD AT IN FRONT OF PUMP HOUSE | ESD.ESD-06.ESD_STATUS | 0 |  |  | ESD.ESD-06.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-07_ESD AT NEAR TANK 04 | ESD-07 | ESD-07 | ESD AT NEAR TANK 04 | ESD.ESD-07.ESD_STATUS | 0 |  |  | ESD.ESD-07.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-08_ESD AT NEAR TANK 28 | ESD-08 | ESD-08 | ESD AT NEAR TANK 28 | ESD.ESD-08.ESD_STATUS | 0 |  |  | ESD.ESD-08.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-09_ESD AT NEAR TANK 17 | ESD-09 | ESD-09 | ESD AT NEAR TANK 17 | ESD.ESD-09.ESD_STATUS | 0 |  |  | ESD.ESD-09.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-10_ESD AT MCC ROOM | ESD-10 | ESD-10 | ESD AT MCC ROOM | ESD.ESD-10.ESD_STATUS | 0 |  |  | ESD.ESD-10.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-11_ESD AT ADMIN BULDING | ESD-11 | ESD-11 | ESD AT ADMIN BULDING | ESD.ESD-11.ESD_STATUS | 0 |  |  | ESD.ESD-11.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-12_ESD AT NEAR ERV SHED | ESD-12 | ESD-12 | ESD AT NEAR ERV SHED | ESD.ESD-12.ESD_STATUS | 0 |  |  | ESD.ESD-12.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-13_ESD FROM PIPE LINE PLC | ESD-13 | PIPELINE ESD | ESD FROM PIPE LINE PLC | ESD.ESD-13.ESD_STATUS | 0 |  |  | ESD.ESD-13.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-14_CENTRAL ESD | ESD-14 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-14.ESD_STATUS | 0 | [6 empty] | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-17_ESD DUE TO RIM SEAL | ESD-17 | ESD-RIMSEAL | ESD DUE TO RIM SEAL | ESD.ESD-17.ESD_STATUS | 0 | [6 empty] | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-18_ESD AT NEAR TK 15 | ESD-18 | ESD-13 | ESD AT NEAR TK 15 | ESD.ESD-18.ESD_STATUS | 0 |  |  | ESD.ESD-18.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-19_ESD AT NEAR TK 01 | ESD-19 | ESD-14 | ESD AT NEAR TK 01 | ESD.ESD-19.ESD_STATUS | 0 |  |  | ESD.ESD-19.MAINTENANCE_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-BPCL_ESD-BPCL | ESD-BPCL | ESD-BPCL | ESD-BPCL | ESD.ESD-BPCL.ESD_STATUS | 0 | [6 empty] | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-IOCL_ESD-IOCL | ESD-IOCL | ESD-IOCL | ESD-IOCL | ESD.ESD-IOCL.ESD_STATUS | 0 | [6 empty] | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 | [6 empty] | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 |  |  | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.TASPLC.ALL_TANKS_IN_DORMANT | 0 |  |  | PLC.SFTPLC.ALL_MOV_CLOSED | 0 |  |  | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 |  |  | PLC.SFTPLC.SIREN_ACTIVATED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 |  |  | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 |  |  | PLC.TASPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1334 | Rewari | ESD-VRU_VRU SKID | ESD-VRU | ESD-VRU | VRU SKID | ESD.ESD-VRU.ESD_STATUS | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | Sensor_Id | Sensor_Type | NO FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | NO FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | LOW FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | LOW FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | HIGH FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | HIGH FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | METER OVERRUN STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BLEND OVERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BLEND UNDERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | ADD OVERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | ADD UNDERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BCU LOADING STATUS | Normal value | Sensor_Id | Sensor_Type | K-FACTOR CHANGE STATUS | Normal value | Sensor_Id | Sensor_Type | K-FACTOR CHANGE STATUS BLEND | Normal value | Sensor_Id | Sensor_Type | BCU VS MFM TOTALIZER MISMATCH | Normal Value | Sensor_Id | Sensor_Type | DAY START TOTALIZER MISMATCH | Normal value | Sensor_Id | Sensor_Type | DAY START TOTALIZER MISMATCH BLEND | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | LP-1_BC-501A_BS VI MS | LP-1 | TLF | BC-501A | BS VI MS | SmartLoad-Dual.BC-501A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-501A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-2_BC-501B_BS VI HSD | LP-2 | TLF | BC-501B | BS VI HSD | SmartLoad-Dual.BC-501B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-501B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-501B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-3_BC-502A_BS VI MS | LP-3 | TLF | BC-502A | BS VI MS | SmartLoad-Dual.BC-502A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-502A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-4_BC-502B_BS VI HSD | LP-4 | TLF | BC-502B | BS VI HSD | SmartLoad-Dual.BC-502B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-502B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-502B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-5_BC-503A_BS VI MS | LP-5 | TLF | BC-503A | BS VI MS | SmartLoad-Dual.BC-503A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-503A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-6_BC-503B_BS VI HSD | LP-6 | TLF | BC-503B | BS VI HSD | SmartLoad-Dual.BC-503B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-503B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-503B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-7_BC-504A_BS VI HSD | LP-7 | TLF | BC-504A | BS VI HSD | SmartLoad-Dual.BC-504A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-504A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-8_BC-504B_BS VI HSD | LP-8 | TLF | BC-504B | BS VI HSD | SmartLoad-Dual.BC-504B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-504B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-504B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-9_BC-505A_BS VI HSD | LP-9 | TLF | BC-505A | BS VI HSD | SmartLoad-Dual.BC-505A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-505A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-505A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-10_BC-505B_BS VI HSD | LP-10 | TLF | BC-505B | BS VI HSD | SmartLoad-Dual.BC-505B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-505B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-505B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-505B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-505B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-505B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-505B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-11_BC-506A_BS VI HSD | LP-11 | TLF | BC-506A | BS VI HSD | SmartLoad-Dual.BC-506A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-506A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-506A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-506A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-506A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-506A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-12_BC-506B_BS VI HSD | LP-12 | TLF | BC-506B | BS VI HSD | SmartLoad-Dual.BC-506B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-506B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-506B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-506B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-506B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-506B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-506B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-13_BC-507A_BS VI MS | LP-13 | TLF | BC-507A | BS VI MS | SmartLoad-Dual.BC-507A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-507A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-507A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-507A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-507A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-507A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-14_BC-507B_BS VI HSD | LP-14 | TLF | BC-507B | BS VI HSD | SmartLoad-Dual.BC-507B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M4 | 0 |  |  | SmartLoad-Dual.BC-507B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-507B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-507B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-15_BC-508A_BS VI HSD | LP-15 | TLF | BC-508A | BS VI HSD | SmartLoad-Dual.BC-508A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | [6 empty] | SmartLoad-Dual.BC-508A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-508A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-508A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-508A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-508A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1334 | Rewari | LP-16_BC-508B_BS VI HSD | LP-16 | TLF | BC-508B | BS VI HSD | SmartLoad-Dual.BC-508B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-508B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-508B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-508B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-508B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-508B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-508B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value | Sensor_Id | Sensor_Type | TLF Product Pumps Stopped | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | Gantry Permissive override | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | Sensor_Id | Sensor_Type | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | Sensor_Id | Sensor_Type | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | Sensor_Id | Sensor_Type | TLF Header Line MOV Close | TLF Header Line MOV Close Normal value | Sensor_Id | Sensor_Type | Hooter activated in control room | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0 | [7 empty] | 0
1334 | Rewari | Gantry Permissive Off |  |  |  |  | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0 |  |  | PLC.TASPLC.ALL_TLF_PUMP_STOPPED | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value | Sensor_Id | Sensor_Type

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Sensor_Id | Sensor_Type | Fire Engine2 | Normal Value | Sensor_Id | Sensor_Type | Fire Engine3 | Normal Value | Sensor_Id | Sensor_Type | Jockey Pump Run1 | Normal Value | Sensor_Id | Sensor_Type | Jockey Pump Run2 | Normal Value | Sensor_Id | Sensor_Type | Farthest Point Pt | Normal value | Sensor_Id | Sensor_Type | Nearest Point PT | Normal value | Sensor_Id | Sensor_Type | Water Volume | Normal value | Sensor_Id | Sensor_Type | Main Fire Engine not in Remote | Normal value | Sensor_Id | Sensor_Type | Jockey Pump1 Remote | Normal value | Sensor_Id | Sensor_Type | Jockey Pump1 Auto | Normal value | Sensor_Id | Sensor_Type | Jockey Pump2 Remote | Normal value | Sensor_Id | Sensor_Type | Jockey Pump2 Auto | Normal value | Sensor_Id | Sensor_Type
1334 | Rewari | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 0 |  |  | PUMP.FWP-02.REMOTE_STATUS | 0 |  |  | PUMP.FWP-03.REMOTE_STATUS | 0 |  |  | PUMP.JCY-01.ON | 1 |  |  | PUMP.JCY-02.ON | 1 |  |  | PressureTransmitter.PT-01.PRESSURE |  |  |  | PressureTransmitter.PT-03.PRESSURE |  |  |  | PLC.TASPLC.TOV_ON_SCREEN | [7 empty] | PUMP.JCY-01.REMOTE_STATUS | 1 |  |  |  | 1 |  |  | PUMP.JCY-02.REMOTE_STATUS | 1 |  |  |  | 1