## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL1 | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS OL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1412 | Hazira | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED RCL | MOV.MOV-01.OPEN_STATUS | 0 | MOV-01 | MOV IL1 | MOV.MOV-01.REMOTE_STATUS | 1 | MOV-01 | MOV IL1 |  |  |  |  | MOV.MOV-02.OPEN_STATUS | 0 | MOV-02 | MOV OL | MOV.MOV-02.REMOTE_STATUS | 1 | MOV-02 | MOV OL |  |  |  |  | MOV.MOV-03.OPEN_STATUS | 0 | MOV-03 | MOV RCL
1412 | Hazira | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV IL1 | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED OL | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED RCL | MOV.MOV-04.OPEN_STATUS | 0 | MOV-04 | MOV IL1 | MOV.MOV-04.REMOTE_STATUS | 1 | MOV-04 | MOV IL1 |  |  |  |  | MOV.MOV-05.OPEN_STATUS | 0 | MOV-05 | MOV OL | MOV.MOV-05.REMOTE_STATUS | 1 | MOV-05 | MOV OL |  |  |  |  | MOV.MOV-06.OPEN_STATUS | 0 | MOV-06 | MOV RCL
1412 | Hazira | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED RCL | MOV.MOV-07.OPEN_STATUS | 0 | MOV-07 | MOV IL1 | MOV.MOV-07.REMOTE_STATUS | 1 | MOV-07 | MOV IL1 |  |  |  |  | MOV.MOV-08.OPEN_STATUS | 0 | MOV-08 | MOV OL | MOV.MOV-08.REMOTE_STATUS | 1 | MOV-08 | MOV OL |  |  |  |  | MOV.MOV-09.OPEN_STATUS | 0 | MOV-09 | MOV RCL
1412 | Hazira | TK-04_ETHANOL | TK-04 | AG | ETHANOL | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV IL1 | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED OL | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED RCL | MOV.MOV-10.OPEN_STATUS | 0 | MOV-10 | MOV IL1 | MOV.MOV-10.REMOTE_STATUS | 1 | MOV-10 | MOV IL1 |  |  |  |  | MOV.MOV-11.OPEN_STATUS | 0 | MOV-11 | MOV OL | MOV.MOV-11.REMOTE_STATUS | 1 | MOV-11 | MOV OL |  |  |  |  | MOV.MOV-12.OPEN_STATUS | 0 | MOV-12 | MOV RCL
1412 | Hazira | TK-05_ETHANOL | TK-05 | AG | ETHANOL | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED RCL | MOV.MOV-13.OPEN_STATUS | 0 | MOV-13 | MOV IL1 | MOV.MOV-13.REMOTE_STATUS | 1 | MOV-13 | MOV IL1 |  |  |  |  | MOV.MOV-14.OPEN_STATUS | 0 | MOV-14 | MOV OL | MOV.MOV-14.REMOTE_STATUS |  | MOV-14 | MOV OL |  |  |  |  | MOV.MOV-15.OPEN_STATUS | 0 | MOV-15 | MOV RCL
1412 | Hazira | TK-06_ETHANOL | TK-06 | AG | ETHANOL | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV IL1 | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED OL | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED RCL | MOV.MOV-16.OPEN_STATUS | 0 | MOV-16 | MOV IL1 | MOV.MOV-16.REMOTE_STATUS | 1 | MOV-16 | MOV IL1 |  |  |  |  | MOV.MOV-17.OPEN_STATUS | 0 | MOV-17 | MOV OL | MOV.MOV-17.REMOTE_STATUS | 1 | MOV-17 | MOV OL |  |  |  |  | MOV.MOV-18.OPEN_STATUS | 0 | MOV-18 | MOV RCL
1412 | Hazira | TK-07_ETHANOL | TK-07 | UG | ETHANOL | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar
1412 | Hazira | TK-08_ETHANOL | TK-08 | UG | ETHANOL | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1412 | Hazira | TK-09_BS VI MS | TK-09 | UG | BS VI MS | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1412 | Hazira | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1412 | Hazira | TK-11_WATER | TK-11 | AG | WATER | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar | [6 empty] | TANK.TK-11.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-12_WATER | TK-12 | AG | WATER | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar | [6 empty] | TANK.TK-12.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-13_WATER | TK-13 | AG | WATER | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar | [6 empty] | TANK.TK-13.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-14_BS VI HSD | TK-14 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED RCL | MOV.MOV-19.OPEN_STATUS | 0 | MOV-19 | MOV IL1 | MOV.MOV-19.REMOTE_STATUS | 1 | MOV-19 | MOV IL1 |  |  |  |  | MOV.MOV-20.OPEN_STATUS | 0 | MOV-20 | MOV OL | MOV.MOV-20.REMOTE_STATUS | 1 | MOV-20 | MOV OL | MOV.MOV-31.OPEN_STATUS | 0 | MOV-31 | MOV OL1 | MOV.MOV-21.OPEN_STATUS | 0 | MOV-21 | MOV RCL
1412 | Hazira | TK-15_BS VI MS | TK-15 | AG | BS VI MS | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV IL1 | MOV.ROSOV-22.FAILED_TO_CLOSE | 0 | ROSOV-22 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-23.FAILED_TO_CLOSE | 0 | ROSOV-23 | ROSOV FAILED OL | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV RCL | MOV.ROSOV-24.FAILED_TO_CLOSE | 0 | ROSOV-24 | ROSOV FAILED RCL | MOV.MOV-22.OPEN_STATUS | 0 | MOV-22 | MOV IL1 | MOV.MOV-22.REMOTE_STATUS | 1 | MOV-22 | MOV IL1 |  |  |  |  | MOV.MOV-23.OPEN_STATUS | 0 | MOV-23 | MOV OL | MOV.MOV-23.REMOTE_STATUS | 1 | MOV-23 | MOV OL | MOV.MOV-32.OPEN_STATUS | 0 | MOV-32 | MOV OL1 | MOV.MOV-24.OPEN_STATUS | 0 | MOV-24 | MOV RCL
1412 | Hazira | TK-21_HHSD | TK-21 | AG | HHSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-21.LEVEL |  | TK-21 | Primary Radar | [6 empty] | TANK.TK-21.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-22_HHSD | TK-22 | AG | HHSD | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-22.LEVEL |  | TK-22 | Primary Radar | [6 empty] | TANK.TK-22.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-23_FO | TK-23 | AG | FO | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-23.LEVEL |  | TK-23 | Primary Radar | [6 empty] | TANK.TK-23.TANK_ALERT_ALARM | 0
1412 | Hazira | TK-24_BS VI MS | TK-24 | AG | BS VI MS | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-24.LEVEL |  | TK-24 | Primary Radar |  |  | TANK.TK-24.HIGH_LEVEL | 0 | TK-24 | Primary Radar | TANK.TK-24.TANK_ALERT_ALARM | 0 | TANK.TK-24.HIGH_HIGH_LEVEL | 0 | TK-24 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | 0 | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-26.OPEN_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | 0 | ROSOV-26 | ROSOV FAILED OL | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV RCL | MOV.ROSOV-27.FAILED_TO_CLOSE | 0 | ROSOV-27 | ROSOV FAILED RCL | MOV.MOV-25.OPEN_STATUS | 0 | MOV-25 | MOV IL1 | MOV.MOV-25.REMOTE_STATUS | 1 | MOV-25 | MOV IL1 |  |  |  |  | MOV.MOV-26.OPEN_STATUS | 0 | MOV-26 | MOV OL | MOV.MOV-26.REMOTE_STATUS | 1 | MOV-26 | MOV OL | MOV.MOV-33.OPEN_STATUS | 0 | MOV-33 | MOV-33 | MOV.MOV-27.OPEN_STATUS | 0 | MOV-27 | MOV RCL
1412 | Hazira | TK-25_BS VI MS | TK-25 | AG | BS VI MS | PLC.SFTPLC.CAUSE_CENTRAL_ESD_ACTIVATED | 0 | TANK.TK-25.LEVEL |  | TK-25 | Primary Radar |  |  | TANK.TK-25.HIGH_LEVEL | 0 | TK-25 | Primary Radar | TANK.TK-25.TANK_ALERT_ALARM | 0 | TANK.TK-25.HIGH_HIGH_LEVEL | 0 | TK-25 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-28.OPEN_STATUS | 0 | ROSOV-28 | ROSOV IL1 | MOV.ROSOV-28.FAILED_TO_CLOSE | 0 | ROSOV-28 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-29.OPEN_STATUS | 0 | ROSOV-29 | ROSOV OL | MOV.ROSOV-29.FAILED_TO_CLOSE | 0 | ROSOV-29 | ROSOV FAILED OL | MOV.ROSOV-30.OPEN_STATUS | 0 | ROSOV-30 | ROSOV RCL | MOV.ROSOV-30.FAILED_TO_CLOSE | 0 | ROSOV-30 | ROSOV FAILED RCL | MOV.MOV-28.OPEN_STATUS | 0 | MOV-28 | MOV IL1 | MOV.MOV-28.REMOTE_STATUS | 1 | MOV-28 | MOV IL1 |  |  |  |  | MOV.MOV-29.OPEN_STATUS | 0 | MOV-29 | MOV OL | MOV.MOV-29.REMOTE_STATUS | 1 | MOV-29 | MOV OL | MOV.MOV-34.OPEN_STATUS | 0 | MOV-34 | MOV-34 | MOV.MOV-30.OPEN_STATUS | 0 | MOV-30 | MOV RCL

## HDR Line MOV
SAPID | Location | Device Name | Product | MOV ID | HDR MOV STATUS | Normal Value | HDR MOV REMOTE STATUS | Normal Value | HDR MOV MAINTENANCE STATUS | Normal Value
1412 | Hazira | TOBV-401_MS-1 | MS-1 | TOBV-401 | MOV.TOBV-401.OPEN_STATUS | TRUE | MOV.TOBV-401.REMOTE_STATUS | TRUE | MOV.TOBV-401.MAINTENANCE_STATUS | FALSE
1412 | Hazira | TOBV-402_MS-2 | MS-2 | TOBV-402 | MOV.TOBV-402.OPEN_STATUS | TRUE | MOV.TOBV-402.REMOTE_STATUS | TRUE | MOV.TOBV-402.MAINTENANCE_STATUS | FALSE
1412 | Hazira | TOBV-403_HSD-1 | HSD-1 | TOBV-403 | MOV.TOBV-403.OPEN_STATUS | TRUE | MOV.TOBV-403.REMOTE_STATUS | TRUE | MOV.TOBV-403.MAINTENANCE_STATUS | FALSE
1412 | Hazira | TOBV-404_HSD-2 | HSD-2 | TOBV-404 | MOV.TOBV-404.OPEN_STATUS | TRUE | MOV.TOBV-404.REMOTE_STATUS | TRUE | MOV.TOBV-404.MAINTENANCE_STATUS | FALSE
1412 | Hazira | TOBV-405_ETH | ETH | TOBV-405 | MOV.TOBV-405.OPEN_STATUS | TRUE | MOV.TOBV-405.REMOTE_STATUS | TRUE | MOV.TOBV-405.MAINTENANCE_STATUS | FALSE

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_id | Sensor_Type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | MOV MAINTENANCE OL1 | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1412 | Hazira_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.MOV-01.MAINTENANCE_STATUS | 0 | MOV-01 | MOV IL1 |  |  |  |  | MOV.MOV-03.MAINTENANCE_STATUS | 0 | MOV-03 | MOV RCL | MOV.MOV-02.MAINTENANCE_STATUS | 0 | MOV-02 | MOV OL
1412 | Hazira_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.MOV-04.MAINTENANCE_STATUS | 0 | MOV-04 | MOV IL1 |  |  |  |  | MOV.MOV-06.MAINTENANCE_STATUS | 0 | MOV-06 | MOV RCL | MOV.MOV-05.MAINTENANCE_STATUS | 0 | MOV-05 | MOV OL
1412 | Hazira_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.MOV-07.MAINTENANCE_STATUS | 0 | MOV-07 | MOV IL1 |  |  |  |  | MOV.MOV-09.MAINTENANCE_STATUS | 0 | MOV-09 | MOV RCL | MOV.MOV-08.MAINTENANCE_STATUS | 0 | MOV-08 | MOV OL
1412 | Hazira_M | TK-04_ETHANOL | TK-04 | AG | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.MOV-10.MAINTENANCE_STATUS | 0 | MOV-10 | MOV IL1 |  |  |  |  | MOV.MOV-12.MAINTENANCE_STATUS | 0 | MOV-12 | MOV RCL | MOV.MOV-11.MAINTENANCE_STATUS | 0 | MOV-11 | MOV OL
1412 | Hazira_M | TK-05_ETHANOL | TK-05 | AG | ETHANOL | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.MOV-13.MAINTENANCE_STATUS | 0 | MOV-13 | MOV IL1 |  |  |  |  | MOV.MOV-15.MAINTENANCE_STATUS | 0 | MOV-15 | MOV RCL | MOV.MOV-14.MAINTENANCE_STATUS | 0 | MOV-14 | MOV OL
1412 | Hazira_M | TK-06_ETHANOL | TK-06 | AG | ETHANOL | TANK.TK-06.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.MOV-16.MAINTENANCE_STATUS | 0 | MOV-16 | MOV IL1 |  |  |  |  | MOV.MOV-18.MAINTENANCE_STATUS | 0 | MOV-18 | MOV RCL | MOV.MOV-17.MAINTENANCE_STATUS | 0 | MOV-17 | MOV OL
1412 | Hazira_M | TK-07_ETHANOL | TK-07 | UG | ETHANOL | TANK.TK-07.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-08_ETHANOL | TK-08 | UG | ETHANOL | TANK.TK-08.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-09_BS VI MS | TK-09 | UG | BS VI MS | TANK.TK-09.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | TANK.TK-10.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-11_WATER | TK-11 | AG | WATER | TANK.TK-11.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-12_WATER | TK-12 | AG | WATER | TANK.TK-12.MAINTENANCE_STATUS | 0
1412 | Hazira_M | TK-13_WATER | TK-13 | AG | WATER | TANK.TK-13.MAINTENANCE_STATUS | 0 | [40 empty] | MOV.MOV-31.MAINTENANCE_STATUS | 0 | MOV-31 | MOV OL1
1412 | Hazira_M | TK-14_BS VI HSD | TK-14 | AG | BS VI HSD | TANK.TK-14.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.MOV-19.MAINTENANCE_STATUS | 0 | MOV-19 | MOV IL1 |  |  |  |  | MOV.MOV-21.MAINTENANCE_STATUS | 0 | MOV-21 | MOV RCL | MOV.MOV-20.MAINTENANCE_STATUS | 0 | MOV-20 | MOV OL | MOV.MOV-32.MAINTENANCE_STATUS | 0 | MOV-32 | MOV OL1
1412 | Hazira_M | TK-15_BS VI MS | TK-15 | AG | BS VI MS | TANK.TK-15.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-22.MAINTENANCE_STATUS | 0 | ROSOV-22 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-23.MAINTENANCE_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-24.MAINTENANCE_STATUS | 0 | ROSOV-24 | ROSOV RCL | MOV.MOV-22.MAINTENANCE_STATUS | 0 | MOV-22 | MOV IL1 |  |  |  |  | MOV.MOV-24.MAINTENANCE_STATUS | 0 | MOV-24 | MOV RCL | MOV.MOV-23.MAINTENANCE_STATUS | 0 | MOV-23 | MOV OL
1412 | Hazira_M | TK-21_HHSD | TK-21 | AG | HHSD
1412 | Hazira_M | TK-22_HHSD | TK-22 | AG | HHSD
1412 | Hazira_M | TK-23_FO | TK-23 | AG | FO | [42 empty] | MOV.MOV-33.MAINTENANCE_STATUS | 0 | MOV-33 | MOV OL1
1412 | Hazira_M | TK-24_BS VI MS | TK-24 | AG | BS VI MS | TANK.TK-24.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-25.MAINTENANCE_STATUS | 0 | ROSOV-25 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-26.MAINTENANCE_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-27.MAINTENANCE_STATUS | 0 | ROSOV-27 | ROSOV RCL | MOV.MOV-25.MAINTENANCE_STATUS | 0 | MOV-25 | MOV IL1 |  |  |  |  | MOV.MOV-27.MAINTENANCE_STATUS | 0 | MOV-27 | MOV RCL | MOV.MOV-26.MAINTENANCE_STATUS | 0 | MOV-26 | MOV OL | MOV.MOV-34.MAINTENANCE_STATUS | 0 | MOV-34 | MOV OL1
1412 | Hazira_M | TK-25_BS VI MS | TK-25 | AG | BS VI MS | TANK.TK-25.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | MOV.ROSOV-28.MAINTENANCE_STATUS | 0 | ROSOV-28 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-29.MAINTENANCE_STATUS | 0 | ROSOV-29 | ROSOV OL | MOV.ROSOV-30.MAINTENANCE_STATUS | 0 | ROSOV-30 | ROSOV RCL | MOV.MOV-28.MAINTENANCE_STATUS | 0 | MOV-28 | MOV IL1 |  |  |  |  | MOV.MOV-30.MAINTENANCE_STATUS | 0 | MOV-30 | MOV RCL | MOV.MOV-29.MAINTENANCE_STATUS | 0 | MOV-29 | MOV OL

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1412 | Hazira | ADTV-PMP-01_TURBOHSD_DISPATCH | ADTV-PMP-01 | TURBOHSD | Truck Loading | DISPATCH | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.OFF | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1412 | Hazira | ADTV-PMP-02_TURBOHSD_DISPATCH | ADTV-PMP-02 | TURBOHSD | Truck Loading | DISPATCH | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.OFF | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1412 | Hazira | ADTV-PMP-03_POWERMS_DISPATCH | ADTV-PMP-03 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.OFF | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1412 | Hazira | ADTV-PMP-04_POWERMS_DISPATCH | ADTV-PMP-04 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.OFF | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-01_BS VI MS_DISPATCH | PMP-01 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.OFF | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-02_BS VI MS_DISPATCH | PMP-02 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.OFF | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-03_ETHANOL_Both | PMP-03 | ETHANOL | Both | Both | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.OFF | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-04_BS VI MS_DISPATCH | PMP-04 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.OFF | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-05_BS VI MS_DISPATCH | PMP-05 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.OFF | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-06_BS VI HSD_DISPATCH | PMP-06 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.OFF | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-07_BS VI HSD_DISPATCH | PMP-07 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.OFF | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-08_BS VI HSD_DISPATCH | PMP-08 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.OFF | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-09_BS VI HSD_DISPATCH | PMP-09 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.OFF | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-10_ETHANOL_Both | PMP-10 | ETHANOL | Both | Both | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.OFF | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-11_ETHANOL_DISPATCH | PMP-11 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.OFF | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1412 | Hazira | PMP-12_ETHANOL_DISPATCH | PMP-12 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.OFF | 0 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-01_BS VI MS_RECEIPT | TWD-01 | BS VI MS | Wagon Loading | RECEIPT | PUMP.TWD-01.ON | 0 | PUMP.TWD-01.OFF | 0 | PUMP.TWD-01.REMOTE_STATUS | 1 | PUMP.TWD-01.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-02_BS VI MS_RECEIPT | TWD-02 | BS VI MS | Wagon Loading | RECEIPT | PUMP.TWD-02.ON | 0 | PUMP.TWD-02.OFF | 0 | PUMP.TWD-02.REMOTE_STATUS | 1 | PUMP.TWD-02.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-03_BS VI MS_RECEIPT | TWD-03 | BS VI MS | Wagon Loading | RECEIPT | PUMP.TWD-03.ON | 0 | PUMP.TWD-03.OFF | 0 | PUMP.TWD-03.REMOTE_STATUS | 1 | PUMP.TWD-03.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-04_BS VI MS_RECEIPT | TWD-04 | BS VI MS | Wagon Loading | RECEIPT | PUMP.TWD-04.ON | 0 | PUMP.TWD-04.OFF | 0 | PUMP.TWD-04.REMOTE_STATUS | 1 | PUMP.TWD-04.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-05_BS VI HSD_RECEIPT | TWD-05 | BS VI HSD | Wagon Loading | RECEIPT | PUMP.TWD-05.ON | 0 | PUMP.TWD-05.OFF | 0 | PUMP.TWD-05.REMOTE_STATUS | 1 | PUMP.TWD-05.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-06_BS VI HSD_RECEIPT | TWD-06 | BS VI HSD | Wagon Loading | RECEIPT | PUMP.TWD-06.ON | 0 | PUMP.TWD-06.OFF | 0 | PUMP.TWD-06.REMOTE_STATUS | 1 | PUMP.TWD-06.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-07_BS VI HSD_RECEIPT | TWD-07 | BS VI HSD | Wagon Loading | RECEIPT | PUMP.TWD-07.ON | 0 | PUMP.TWD-07.OFF | 0 | PUMP.TWD-07.REMOTE_STATUS | 1 | PUMP.TWD-07.MAINTENANCE_STATUS | 0
1412 | Hazira | TWD-08_BS VI HSD_RECEIPT | TWD-08 | BS VI HSD | Wagon Loading | RECEIPT | PUMP.TWD-08.ON | 0 | PUMP.TWD-08.OFF | 0 | PUMP.TWD-08.REMOTE_STATUS | 1 | PUMP.TWD-08.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1412 | Hazira | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.OFF | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1412 | Hazira | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.OFF | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1412 | Hazira | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.OFF | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1412 | Hazira | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.OFF | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0
1412 | Hazira | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.OFF | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0
1412 | Hazira | Farthest Point PT_WATER Pressure_FIRE HYDRANT | Farthest Point PT | WATER Pressure | PT | FIRE HYDRANT | [6 empty] | PressureTransmitter.FPT-01.MAINTENANCE_STATUS | 0
1412 | Hazira | Nearest Point PT_WATER Pressure_FIRE HYDRANT | Nearest Point PT | WATER Pressure | PT | FIRE HYDRANT | [6 empty] | PressureTransmitter.FPT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1412 | Hazira | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-301.LOW_BATTERY | 0 | UPS.UPS-301.LOAD_ON_UPS | 0 | UPS.UPS-301.MAIN_AC_FAIL | 0
1412 | Hazira | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-302.LOW_BATTERY | 0 | UPS.UPS-302.LOAD_ON_UPS | 0 | UPS.UPS-302.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1412 | Hazira | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1412 | Hazira | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB | [8 empty] | PLC.SFTPLC.PLCA_COMM_OK | 0 |  |  | PLC.SFTPLC.PLCB_COMM_OK | 0

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1412 | Hazira | HCD-01_OPEN-HCD-101_OPD TK24 | HCD-01 | OPEN-HCD-101 | OPD TK24 | GDS.HCD-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-01.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-02_OPEN-HCD-102_OPD TLF PH | HCD-02 | OPEN-HCD-102 | OPD TLF PH | GDS.HCD-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-02.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-03_OPEN-HCD-103_OPD TK5 | HCD-03 | OPEN-HCD-103 | OPD TK5 | GDS.HCD-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-03.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-04_OPEN-HCD-104_FIXED TWD PH NEAR TK15 | HCD-04 | OPEN-HCD-104 | FIXED TWD PH NEAR TK15 | GDS.HCD-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-04.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-05_OPEN-HCD-105_OPD TWD | HCD-05 | OPEN-HCD-105 | OPD TWD | GDS.HCD-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-05.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-06_POINT-HCD-101_PTD TK24 | HCD-06 | POINT-HCD-101 | PTD TK24 | GDS.HCD-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-06.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-07_POINT-HCD-102_PTD TK05 | HCD-07 | POINT-HCD-102 | PTD TK05 | GDS.HCD-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-07.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-08_POINT-HCD-103_TLF PH | HCD-08 | POINT-HCD-103 | TLF PH | GDS.HCD-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-08.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-09_POINT-HCD-104_OPD TLF PH NEAR TK4 | HCD-09 | POINT-HCD-104 | OPD TLF PH NEAR TK4 | GDS.HCD-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-09.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-10_POINT-HCD-105_OPD TK15 | HCD-10 | POINT-HCD-105 | OPD TK15 | GDS.HCD-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-10.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-11_FIXED-HCD-TK01_FIXED-HCD-TK01 | HCD-11 | FIXED-HCD-TK01 | FIXED-HCD-TK01 | GDS.HCD-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-11.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-11.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HCD-12_FIXED-HCD-TK15_FIXED-HCD-TK15 | HCD-12 | FIXED-HCD-TK15 | FIXED-HCD-TK15 | GDS.HCD-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-12.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-12.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1412 | Hazira | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1412 | Hazira | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1412 | Hazira | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1412 | Hazira | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1412 | Hazira | DV-05 | DRAINVALVE.DV-05.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1412 | Hazira | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.CLOSE_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1412 | Hazira | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.CLOSE_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1412 | Hazira | HOOTER 1_HOOTER_FIELD_1 | HOOTER 1 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1412 | Hazira | HOOTER 2_HOOTER_FIELD_2 | HOOTER 2 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1412 | Hazira | HOOTER 3_HOOTER_FIELD_3 | HOOTER 3 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1412 | Hazira | HOOTER 4_HOOTER_FIELD_4 | HOOTER 4 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1412 | Hazira | HOOTER 5_HOOTER_FOR_HC_CR | HOOTER 5 | HOOTER_FOR_HC_CR | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1412 | Hazira | HOOTER 6_HOOTER_FOR_RIMSEAL_CR | HOOTER 6 | HOOTER_FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1412 | Hazira | ESD-01_NEAR TK-14 | ESD-01 | ESD-01 | NEAR TK-14 | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-02_ADMIN BUILDING | ESD-02 | ESD-02 | ADMIN BUILDING | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-03_TLF PUMP HOUSE-1 | ESD-03 | ESD-03 | TLF PUMP HOUSE-1 | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-04_TLF GANTRY_CABIN | ESD-04 | ESD-04 | TLF GANTRY_CABIN | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-05_SPARE | ESD-05 | ESD-05 | SPARE | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-06_TLF PUMP HOUSE-2 | ESD-06 | ESD-06 | TLF PUMP HOUSE-2 | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-07_NEAR TK-03 | ESD-07 | ESD-07 | NEAR TK-03 | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-08_NEAR TK-06 | ESD-08 | ESD-08 | NEAR TK-06 | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-09_NEAR TK-15 | ESD-09 | ESD-09 | NEAR TK-15 | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-10_WAGON SIDING | ESD-10 | ESD-10 | WAGON SIDING | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-11_TM ROOM | ESD-11 | ESD-11 | TM ROOM | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-12_CONTROL ROOM | ESD-12 | ESD-12 | CONTROL ROOM | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-13_NEAR TK-23 | ESD-13 | ESD-13 | NEAR TK-23 | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-14_SPARE | ESD-14 | ESD-14 | SPARE | ESD.ESD-14.ESD_STATUS | 0 | ESD.ESD-14.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-15_WAGON PH | ESD-15 | ESD-15 | WAGON PH | ESD.ESD-15.ESD_STATUS | 0 | ESD.ESD-15.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-16_SECURITY GATE | ESD-16 | ESD-16 | SECURITY GATE | ESD.ESD-16.ESD_STATUS | 0 | ESD.ESD-16.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-CENTRAL_ESD-CENTRAL | ESD-CENTRAL | CENTRAL ESD | ESD-CENTRAL | ESD.ESD-CENTRAL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1412 | Hazira | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PPLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1412 | Hazira | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 02_BC-01B_BS VI HSD | LP 02 | TLF | BC-01B | BS VI HSD | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 03_BC-02A_BS VI MS | LP 03 | TLF | BC-02A | BS VI MS | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 04_BC-02B_BS VI HSD | LP 04 | TLF | BC-02B | BS VI HSD | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 05_BC-03A_BS VI MS | LP 05 | TLF | BC-03A | BS VI MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 07_BC-04A_BS VI HSD | LP 07 | TLF | BC-04A | BS VI HSD | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 09_BC-05A_BS VI MS | LP 09 | TLF | BC-05A | BS VI MS | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 11_BC-06A_BS VI MS | LP 11 | TLF | BC-06A | BS VI MS | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 13_BC-07A_BS VI MS | LP 13 | TLF | BC-07A | BS VI MS | SmartLoad-Dual.BC-07A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 14_BC-07B_BS VI HSD | LP 14 | TLF | BC-07B | BS VI HSD | SmartLoad-Dual.BC-07B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-07B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 15_BC-08A_BS VI HSD | LP 15 | TLF | BC-08A | BS VI HSD | SmartLoad-Dual.BC-08A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-08A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-08A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1412 | Hazira | LP 16_BC-08B_BS VI HSD | LP 16 | TLF | BC-08B | BS VI HSD | SmartLoad-Dual.BC-08B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-08B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1412 | Hazira | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1412 | Hazira | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1412 | Hazira | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1412 | Hazira | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1412 | Hazira | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1412 | Hazira | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1412 | Hazira | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1412 | Hazira | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1412 | Hazira | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.FPT-02.PRESSURE |  | PressureTransmitter.FPT-01.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 |  |  | PUMP.JCY-02.REMOTE_STATUS | 1