## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS OL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1856 | Coimbatore | TK-01_ATF | TK-01 | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | [8 empty] | MOV.MOV-001.OPEN_STATUS | 0 | MOV-001 | MOV IL1 | MOV.MOV-001.REMOTE_STATUS | 1 | MOV-001 | MOV IL1 |  |  |  |  | MOV.MOV-002.OPEN_STATUS | 0 | MOV-002 | MOV OL | MOV.MOV-002.REMOTE_STATUS | 1 | MOV-002 | MOV OL
1856 | Coimbatore | TK-02_ATF | TK-02 | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED OL | [8 empty] | MOV.MOV-003.OPEN_STATUS | 0 | MOV-003 | MOV IL1 | MOV.MOV-003.REMOTE_STATUS | 1 | MOV-003 | MOV IL1 |  |  |  |  | MOV.MOV-004.OPEN_STATUS | 0 | MOV-004 | MOV OL | MOV.MOV-004.REMOTE_STATUS | 1 | MOV-004 | MOV OL
1856 | Coimbatore | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED OL | [8 empty] | MOV.MOV-005.OPEN_STATUS | 0 | MOV-005 | MOV IL1 | MOV.MOV-005.REMOTE_STATUS | 1 | MOV-005 | MOV IL1 |  |  |  |  | MOV.MOV-006.OPEN_STATUS | 0 | MOV-006 | MOV OL | MOV.MOV-006.REMOTE_STATUS | 1 | MOV-006 | MOV OL
1856 | Coimbatore | TK-04_BS VI MS | TK-04 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.MOV-007.OPEN_STATUS | 0 | MOV-007 | MOV IL1 | MOV.MOV-007.REMOTE_STATUS | 1 | MOV-007 | MOV IL1 |  |  |  |  | MOV.MOV-008.OPEN_STATUS | 0 | MOV-008 | MOV OL | MOV.MOV-008.REMOTE_STATUS | 1 | MOV-008 | MOV OL
1856 | Coimbatore | TK-05_BS VI MS | TK-05 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL | [8 empty] | MOV.MOV-009.OPEN_STATUS | 0 | MOV-009 | MOV IL1 | MOV.MOV-009.REMOTE_STATUS | 1 | MOV-009 | MOV IL1 |  |  |  |  | MOV.MOV-010.OPEN_STATUS | 0 | MOV-010 | MOV OL | MOV.MOV-010.REMOTE_STATUS | 1 | MOV-010 | MOV OL
1856 | Coimbatore | TK-06_ETHANOL | TK-06 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED OL | [8 empty] | MOV.MOV-011.OPEN_STATUS | 0 | MOV-011 | MOV IL1 | MOV.MOV-011.REMOTE_STATUS | 1 | MOV-011 | MOV IL1 |  |  |  |  | MOV.MOV-012.OPEN_STATUS | 0 | MOV-012 | MOV OL | MOV.MOV-012.REMOTE_STATUS | 1 | MOV-012 | MOV OL
1856 | Coimbatore | TK-07_ETHANOL | TK-07 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar
1856 | Coimbatore | TK-08_ETHANOL | TK-08 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1856 | Coimbatore | TK-09_BS VI HSD | TK-09 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1856 | Coimbatore | TK-10_WATER | TK-10 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1856 | Coimbatore | TK-11_WATER | TK-11 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar |  |  | TANK.TK-11.TANK_ALERT_ALARM | 0 | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar
1856 | Coimbatore | TK-12_BS VI MS | TK-12 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.TANK_ALERT_ALARM | 0 | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | [8 empty] | MOV.MOV-013.OPEN_STATUS | 0 | MOV-013 | MOV IL1 | MOV.MOV-013.REMOTE_STATUS | 1 | MOV-013 | MOV IL1 |  |  |  |  | MOV.MOV-014.OPEN_STATUS | 0 | MOV-014 | MOV OL | MOV.MOV-014.REMOTE_STATUS | 1 | MOV-014 | MOV OL
1856 | Coimbatore | TK-13_ATF | TK-13 | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.TANK_ALERT_ALARM | 0 | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar | LEVELSWITCH.LSW-11.SWITCH_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_OK | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_FAILED | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.SWITCH_STATUS | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_OK | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_FAILED | 0 | RDR-11 | RADAR | MOV.ROSOV-39.OPEN_STATUS | 0 | ROSOV-39 | ROSOV IL1 | MOV.ROSOV-39.FAILED_TO_CLOSE | 0 | ROSOV-39 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-40.OPEN_STATUS | 0 | ROSOV-40 | ROSOV OL | MOV.ROSOV-40.FAILED_TO_CLOSE | 0 | ROSOV-40 | ROSOV FAILED OL | [8 empty] | MOV.MOV-032.OPEN_STATUS | 0 | MOV-032 | MOV IL1 | MOV.MOV-032.REMOTE_STATUS | 1 | MOV-032 | MOV IL1 |  |  |  |  | MOV.MOV-033.OPEN_STATUS | 0 | MOV-033 | MOV OL | MOV.MOV-033.REMOTE_STATUS | 1 | MOV-033 | MOV OL
1856 | Coimbatore | TK-14_ETHANOL | TK-14 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV OL | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED OL | [8 empty] | MOV.MOV-015.OPEN_STATUS | 0 | MOV-015 | MOV IL1 | MOV.MOV-015.REMOTE_STATUS | 1 | MOV-015 | MOV IL1 |  |  |  |  | MOV.MOV-016.OPEN_STATUS | 0 | MOV-016 | MOV OL | MOV.MOV-016.REMOTE_STATUS | 1 | MOV-016 | MOV OL
1856 | Coimbatore | TK-15_BS VI HSD | TK-15 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV IL1 | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV OL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED OL | [8 empty] | MOV.MOV-017.OPEN_STATUS | 0 | MOV-017 | MOV IL1 | MOV.MOV-017.REMOTE_STATUS | 1 | MOV-017 | MOV IL1 |  |  |  |  | MOV.MOV-018.OPEN_STATUS | 0 | MOV-018 | MOV OL | MOV.MOV-018.REMOTE_STATUS | 1 | MOV-018 | MOV OL
1856 | Coimbatore | TK-16_BS VI HSD | TK-16 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar |  |  | TANK.TK-16.TANK_ALERT_ALARM | 0 | TANK.TK-16.HIGH_LEVEL | 0 | TK-16 | Primary Radar | TANK.TK-16.HIGH_HIGH_LEVEL | 0 | TK-16 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | [8 empty] | MOV.MOV-019.OPEN_STATUS | 0 | MOV-019 | MOV IL1 | MOV.MOV-019.REMOTE_STATUS | 1 | MOV-019 | MOV IL1 |  |  |  |  | MOV.MOV-020.OPEN_STATUS | 0 | MOV-020 | MOV OL | MOV.MOV-020.REMOTE_STATUS | 1 | MOV-020 | MOV OL
1856 | Coimbatore | TK-18_LDO | TK-18 | AG | LDO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-18.LEVEL |  | TK-18 | Primary Radar |  |  | TANK.TK-18.TANK_ALERT_ALARM | 0 | TANK.TK-18.HIGH_LEVEL | 0 | TK-18 | Primary Radar | TANK.TK-18.HIGH_HIGH_LEVEL | 0 | TK-18 | Primary Radar
1856 | Coimbatore | TK-19_ETHANOL | TK-19 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-19.LEVEL |  | TK-19 | Primary Radar |  |  | TANK.TK-19.TANK_ALERT_ALARM | 0 | TANK.TK-19.HIGH_LEVEL | 0 | TK-19 | Primary Radar | TANK.TK-19.HIGH_HIGH_LEVEL | 0 | TK-19 | Primary Radar
1856 | Coimbatore | TK-20_BS VI HSD | TK-20 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-20.LEVEL |  | TK-20 | Primary Radar |  |  | TANK.TK-20.TANK_ALERT_ALARM | 0 | TANK.TK-20.HIGH_LEVEL | 0 | TK-20 | Primary Radar | TANK.TK-20.HIGH_HIGH_LEVEL | 0 | TK-20 | Primary Radar
1856 | Coimbatore | TK-21_BS VI HSD | TK-21 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-21.LEVEL |  | TK-21 | Primary Radar |  |  | TANK.TK-21.TANK_ALERT_ALARM | 0 | TANK.TK-21.HIGH_LEVEL | 0 | TK-21 | Primary Radar | TANK.TK-21.HIGH_HIGH_LEVEL | 0 | TK-21 | Primary Radar
1856 | Coimbatore | TK-22_BS VI MS | TK-22 | UG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-22.LEVEL |  | TK-22 | Primary Radar |  |  | TANK.TK-22.TANK_ALERT_ALARM | 0 | TANK.TK-22.HIGH_LEVEL | 0 | TK-22 | Primary Radar | TANK.TK-22.HIGH_HIGH_LEVEL | 0 | TK-22 | Primary Radar
1856 | Coimbatore | TK-23_ATF | TK-23 | UG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | - | [5 empty] | TANK.TK-23.TANK_ALERT_ALARM | 0 | TANK.TK-23.HIGH_LEVEL | 0 | TK-23 | Primary Radar | TANK.TK-23.HIGH_HIGH_LEVEL | 0 | TK-23 | Primary Radar | LEVELSWITCH.LSW-12.SWITCH_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_OK | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_FAILED | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.SWITCH_STATUS | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_OK | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_FAILED | 0 | RDR-12 | RADAR | MOV.ROSOV-41.OPEN_STATUS | 0 | ROSOV-41 | ROSOV IL1 | MOV.ROSOV-41.FAILED_TO_CLOSE | 0 | ROSOV-41 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-42.OPEN_STATUS | 0 | ROSOV-42 | ROSOV OL | MOV.ROSOV-42.FAILED_TO_CLOSE | 0 | ROSOV-42 | ROSOV FAILED OL | [8 empty] | MOV.MOV-034.OPEN_STATUS | 0 | MOV-034 | MOV IL1 | MOV.MOV-034.REMOTE_STATUS | 1 | MOV-034 | MOV IL1 |  |  |  |  | MOV.MOV-035.OPEN_STATUS | 0 | MOV-035 | MOV OL | MOV.MOV-035.REMOTE_STATUS | 1 | MOV-035 | MOV OL
1856 | Coimbatore | TK-24_ATF | TK-24 | UG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | - | [5 empty] | TANK.TK-24.TANK_ALERT_ALARM | 0 | TANK.TK-24.HIGH_LEVEL | 0 | TK-24 | Primary Radar | TANK.TK-24.HIGH_HIGH_LEVEL | 0 | TK-24 | Primary Radar | LEVELSWITCH.LSW-13.SWITCH_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_OK | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_FAILED | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.SWITCH_STATUS | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_OK | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_FAILED | 0 | RDR-13 | RADAR | MOV.ROSOV-43.OPEN_STATUS | 0 | ROSOV-43 | ROSOV IL1 | MOV.ROSOV-43.FAILED_TO_CLOSE | 0 | ROSOV-43 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-44.OPEN_STATUS | 0 | ROSOV-44 | ROSOV OL | MOV.ROSOV-44.FAILED_TO_CLOSE | 0 | ROSOV-44 | ROSOV FAILED OL | [8 empty] | MOV.MOV-036.OPEN_STATUS | 0 | MOV-036 | MOV IL1 | MOV.MOV-036.REMOTE_STATUS | 1 | MOV-036 | MOV IL1 |  |  |  |  | MOV.MOV-037.OPEN_STATUS | 0 | MOV-037 | MOV OL | MOV.MOV-037.REMOTE_STATUS | 1 | MOV-037 | MOV OL
1856 | Coimbatore | TK-29_BIO DIESEL | TK-29 | UG | BIO DIESEL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-29.LEVEL |  | TK-29 | Primary Radar |  |  | TANK.TK-29.TANK_ALERT_ALARM | 0 | TANK.TK-29.HIGH_LEVEL | 0 | TK-29 | Primary Radar | TANK.TK-29.HIGH_HIGH_LEVEL | 0 | TK-29 | Primary Radar
1856 | Coimbatore | TK-30_BIO DIESEL | TK-30 | UG | BIO DIESEL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-30.LEVEL |  | TK-30 | Primary Radar |  |  | TANK.TK-30.TANK_ALERT_ALARM | 0 | TANK.TK-30.HIGH_LEVEL | 0 | TK-30 | Primary Radar | TANK.TK-30.HIGH_HIGH_LEVEL | 0 | TK-30 | Primary Radar

## HDR Line MOV
SAPID | Location | Device Name | Product | MOV ID | HDR MOV STATUS | Normal Value | HDR MOV REMOTE STATUS | Normal Value | HDR MOV MAINTENANCE STATUS | Normal Value
1856 | Coimbatore | TOBV-01_BS VI HSD | BS VI HSD | TOBV-01 | MOV.TOBV-01.OPEN_STATUS | TRUE | MOV.TOBV-01.REMOTE_STATUS | TRUE | MOV.TOBV-01.MAINTENANCE_STATUS | FALSE
1856 | Coimbatore | TOBV-02_BIO DIESEL | BIO DIESEL | TOBV-02 | MOV.TOBV-02.OPEN_STATUS | TRUE | MOV.TOBV-02.REMOTE_STATUS | TRUE | MOV.TOBV-02.MAINTENANCE_STATUS | FALSE
1856 | Coimbatore | TOBV-03_ATF | ATF | TOBV-03 | MOV.TOBV-03.OPEN_STATUS | TRUE | MOV.TOBV-03.REMOTE_STATUS | TRUE | MOV.TOBV-03.MAINTENANCE_STATUS | FALSE
1856 | Coimbatore | TOBV-04_ETHANOL | ETHANOL | TOBV-04 | MOV.TOBV-04.OPEN_STATUS | TRUE | MOV.TOBV-04.REMOTE_STATUS | TRUE | MOV.TOBV-04.MAINTENANCE_STATUS | FALSE
1856 | Coimbatore | TOBV-05_BS VI MS | BS VI MS | TOBV-05 | MOV.TOBV-05.OPEN_STATUS | TRUE | MOV.TOBV-05.REMOTE_STATUS | TRUE | MOV.TOBV-05.MAINTENANCE_STATUS | FALSE

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1856 | Coimbatore_M | TK-01_ATF | TK-01 | AG | ATF | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL |  |  |  |  | MOV.MOV-001.MAINTENANCE_STATUS | 0 | MOV-001 | MOV IL1 | [8 empty] | MOV.MOV-002.MAINTENANCE_STATUS | 0 | MOV-002 | MOV OL
1856 | Coimbatore_M | TK-02_ATF | TK-02 | AG | ATF | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV OL |  |  |  |  | MOV.MOV-003.MAINTENANCE_STATUS | 0 | MOV-003 | MOV IL1 | [8 empty] | MOV.MOV-004.MAINTENANCE_STATUS | 0 | MOV-004 | MOV OL
1856 | Coimbatore_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV OL |  |  |  |  | MOV.MOV-005.MAINTENANCE_STATUS | 0 | MOV-005 | MOV IL1 | [8 empty] | MOV.MOV-006.MAINTENANCE_STATUS | 0 | MOV-006 | MOV OL
1856 | Coimbatore_M | TK-04_BS VI MS | TK-04 | AG | BS VI MS | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL |  |  |  |  | MOV.MOV-007.MAINTENANCE_STATUS | 0 | MOV-007 | MOV IL1 | [8 empty] | MOV.MOV-008.MAINTENANCE_STATUS | 0 | MOV-008 | MOV OL
1856 | Coimbatore_M | TK-05_BS VI MS | TK-05 | AG | BS VI MS | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV OL |  |  |  |  | MOV.MOV-009.MAINTENANCE_STATUS | 0 | MOV-009 | MOV IL1 | [8 empty] | MOV.MOV-010.MAINTENANCE_STATUS | 0 | MOV-010 | MOV OL
1856 | Coimbatore_M | TK-06_ETHANOL | TK-06 | AG | ETHANOL | TANK.TK-06.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV OL |  |  |  |  | MOV.MOV-011.MAINTENANCE_STATUS | 0 | MOV-011 | MOV IL1 | [8 empty] | MOV.MOV-012.MAINTENANCE_STATUS | 0 | MOV-012 | MOV OL
1856 | Coimbatore_M | TK-12_BS VI MS | TK-12 | AG | BS VI MS | TANK.TK-12.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL |  |  |  |  | MOV.MOV-013.MAINTENANCE_STATUS | 0 | MOV-013 | MOV IL1 | [8 empty] | MOV.MOV-014.MAINTENANCE_STATUS | 0 | MOV-014 | MOV OL
1856 | Coimbatore_M | TK-13_ATF | TK-13 | AG | ATF | TANK.TK-13.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-11.MAINTENANCE_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.MAINTENANCE_STATUS | 0 | RDR-11 | RADAR | MOV.ROSOV-39.MAINTENANCE_STATUS | 0 | ROSOV-39 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-40.MAINTENANCE_STATUS | 0 | ROSOV-40 | ROSOV OL |  |  |  |  | MOV.MOV-032.MAINTENANCE_STATUS | 0 | MOV-032 | MOV IL1 | [8 empty] | MOV.MOV-033.MAINTENANCE_STATUS | 0 | MOV-033 | MOV OL
1856 | Coimbatore_M | TK-14_ETHANOL | TK-14 | AG | ETHANOL | TANK.TK-14.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV OL |  |  |  |  | MOV.MOV-015.MAINTENANCE_STATUS | 0 | MOV-015 | MOV IL1 | [8 empty] | MOV.MOV-016.MAINTENANCE_STATUS | 0 | MOV-016 | MOV OL
1856 | Coimbatore_M | TK-15_BS VI HSD | TK-15 | AG | BS VI HSD | TANK.TK-15.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV OL |  |  |  |  | MOV.MOV-017.MAINTENANCE_STATUS | 0 | MOV-017 | MOV IL1 | [8 empty] | MOV.MOV-018.MAINTENANCE_STATUS | 0 | MOV-018 | MOV OL
1856 | Coimbatore_M | TK-16_BS VI HSD | TK-16 | AG | BS VI HSD | TANK.TK-16.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL |  |  |  |  | MOV.MOV-019.MAINTENANCE_STATUS | 0 | MOV-019 | MOV IL1 | [8 empty] | MOV.MOV-020.MAINTENANCE_STATUS | 0 | MOV-020 | MOV OL
1856 | Coimbatore_M | TK-23_ATF | TK-23 | UG | ATF | TANK.TK-23.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-12.MAINTENANCE_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.MAINTENANCE_STATUS | 0 | RDR-12 | RADAR | MOV.ROSOV-41.MAINTENANCE_STATUS | 0 | ROSOV-41 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-42.MAINTENANCE_STATUS | 0 | ROSOV-42 | ROSOV OL |  |  |  |  | MOV.MOV-034.MAINTENANCE_STATUS | 0 | MOV-034 | MOV IL1 | [8 empty] | MOV.MOV-035.MAINTENANCE_STATUS | 0 | MOV-035 | MOV OL
1856 | Coimbatore_M | TK-24_ATF | TK-24 | UG | ATF | TANK.TK-24.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-13.MAINTENANCE_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.MAINTENANCE_STATUS | 0 | RDR-13 | RADAR | MOV.ROSOV-43.MAINTENANCE_STATUS | 0 | ROSOV-43 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-44.MAINTENANCE_STATUS | 0 | ROSOV-44 | ROSOV OL |  |  |  |  | MOV.MOV-036.MAINTENANCE_STATUS | 0 | MOV-036 | MOV IL1 | [8 empty] | MOV.MOV-037.MAINTENANCE_STATUS | 0 | MOV-037 | MOV OL

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1856 | Coimbatore | PMP-01_BS VI HSD_DISPATCH | PMP-01 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-02_BS VI HSD_DISPATCH | PMP-02 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-03_BS VI HSD_DISPATCH | PMP-03 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | Wagon Loading | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-05_BS VI MS_DISPATCH | PMP-05 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-06_BS VI MS_DISPATCH | PMP-06 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-07_BS VI MS_DISPATCH | PMP-07 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-08_BS VI MS_DISPATCH | PMP-08 | BS VI MS | Wagon Loading | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-09_BS VI MS_DISPATCH | PMP-09 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-11_SKO_DISPATCH | PMP-11 | SKO | Wagon Loading | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-18_ETHANOL_DISPATCH | PMP-18 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-18.ON | 0 | PUMP.PMP-18.REMOTE_STATUS | 1 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-19_ETHANOL_DISPATCH | PMP-19 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-19.ON | 0 | PUMP.PMP-19.REMOTE_STATUS | 1 | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-20_POWERMS_DISPATCH | PMP-20 | POWERMS | Truck Loading | DISPATCH | PUMP.PMP-20.ON | 0 | PUMP.PMP-20.REMOTE_STATUS | 1 | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-21_TURBOHSD_DISPATCH | PMP-21 | TURBOHSD | Truck Loading | DISPATCH | PUMP.PMP-21.ON | 0 | PUMP.PMP-21.REMOTE_STATUS | 1 | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-22_POWERMS_DISPATCH | PMP-22 | POWERMS | Truck Loading | DISPATCH | PUMP.PMP-22.ON | 0 | PUMP.PMP-22.REMOTE_STATUS | 1 | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-23_TURBOHSD_DISPATCH | PMP-23 | TURBOHSD | Truck Loading | DISPATCH | PUMP.PMP-23.ON | 0 | PUMP.PMP-23.REMOTE_STATUS | 1 | PUMP.PMP-23.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-24_BS VI HSD_DISPATCH | PMP-24 | BS VI HSD | Wagon Loading | DISPATCH | PUMP.PMP-24.ON | 0 | PUMP.PMP-24.REMOTE_STATUS | 1 | PUMP.PMP-24.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-25_BS VI MS_DISPATCH | PMP-25 | BS VI MS | Wagon Loading | DISPATCH | PUMP.PMP-25.ON | 0 | PUMP.PMP-25.REMOTE_STATUS | 1 | PUMP.PMP-25.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-26_ETHANOL_DISPATCH | PMP-26 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-26.ON | 0 | PUMP.PMP-26.REMOTE_STATUS | 1 | PUMP.PMP-26.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-27_BS VI HSD_DISPATCH | PMP-27 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-27.ON | 0 | PUMP.PMP-27.REMOTE_STATUS | 1 | PUMP.PMP-27.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-28_ATF_DISPATCH | PMP-28 | ATF | Truck Loading | DISPATCH | PUMP.PMP-28.ON | 0 | PUMP.PMP-28.REMOTE_STATUS | 1 | PUMP.PMP-28.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-29_ATF_DISPATCH | PMP-29 | ATF | Truck Loading | DISPATCH | PUMP.PMP-29.ON | 0 | PUMP.PMP-29.REMOTE_STATUS | 1 | PUMP.PMP-29.MAINTENANCE_STATUS | 0
1856 | Coimbatore | PMP-30_ATF_DISPATCH | PMP-30 | ATF | Truck Loading | DISPATCH | PUMP.PMP-30.ON | 0 | PUMP.PMP-30.REMOTE_STATUS | 1
1856 | Coimbatore | PMP-31_ATF_DISPATCH | PMP-31 | ATF | Truck Loading | DISPATCH | PUMP.PMP-31.ON | 0 | PUMP.PMP-31.REMOTE_STATUS | 1

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction | PUMP ON STATUS | Normal value | PUMP LR STATUS | Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | Normal value | FIRE PUMP FAIL TO START 2 | Normal value | FIRE PUMP FAIL TO START 3 | Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP TRIPPED FAULT | Normal value | FIRE PUMP LLOP ALARM | Normal value | FIRE PUMP HWT ALARM | Normal value
1856 | Coimbatore | FWP-01_Water_DISPATCH | FWP-01 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1856 | Coimbatore | FWP-02_Water_DISPATCH | FWP-02 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1856 | Coimbatore | FWP-03_Water_DISPATCH | FWP-03 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1856 | Coimbatore | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-01.PUMP_TRIPPED | 0
1856 | Coimbatore | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-02.PUMP_TRIPPED | 0
1856 | Coimbatore | Farthest Point PT_WATER Pressure_Near Tank no. 01 | Farthest Point PT | WATER Pressure | PT | Near Tank no. 01 |  |  |  |  | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1856 | Coimbatore | Nearest Point PT_WATER Pressure_FWP pump house | Nearest Point PT | WATER Pressure | PT | FWP pump house |  |  |  |  | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | Normal Value | LOW BATTERY | Normal Value | UPS ON | Normal Value | UPS MAIN AC FAIL | Normal Value
1856 | Coimbatore | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.LOAD_ON_UPS | 0 | UPS.UPS-01.MAIN_AC_FAIL | 0
1856 | Coimbatore | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.LOAD_ON_UPS | 0 | UPS.UPS-02.MAIN_AC_FAIL | 0
1856 | Coimbatore | UPS-03_Control Room | UPS-03 | Control Room |  |  | UPS.UPS-03.LOW_BATTERY | 0 | UPS.UPS-03.UPS_ON | 0 | UPS.UPS-03.MAIN_AC_FAIL | 0
1856 | Coimbatore | UPS-04_Control Room | UPS-04 | Control Room |  |  | UPS.UPS-04.LOW_BATTERY | 0 | UPS.UPS-04.UPS_ON | 0 | UPS.UPS-04.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1856 | Coimbatore | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1856 | Coimbatore | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB | PLC.SFTPLC.PLCA_FAIL_SAFE_STATUS | 0 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLCB | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | Normal Value | HCD 20 % ALARM | Normal Value | HCD FAULT | Normal Value | MISALIGNMENT FAULT | Normal Value | HCD MAINTENANCE | Normal Value | HCD Hooter Activated | Normal value
1856 | Coimbatore | HDS-01_OPENPATH_TANK - 05 | HDS-01 | OPENPATH | TANK - 05 | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-02_OPENPATH_TTL PUMP HOUSE | HDS-02 | OPENPATH | TTL PUMP HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-03_OPENPATH_TWL PUMP HOUSE | HDS-03 | OPENPATH | TWL PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-04_OPENPATH_TANK - 14 | HDS-04 | OPENPATH | TANK - 14 | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-05_OPENPATH_TANK - 12 | HDS-05 | OPENPATH | TANK - 12 | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-06_OPENPATH_TANK - 06 | HDS-06 | OPENPATH | TANK - 06 | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-07_FIXEDTYPE_TANK - 05 / 06 | HDS-07 | FIXEDTYPE | TANK - 05 / 06 | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-08_FIXEDTYPE_TANK - 12 / 14 | HDS-08 | FIXEDTYPE | TANK - 12 / 14 | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-09_POINTTYPE_TANK 12 MOV | HDS-09 | POINTTYPE | TANK 12 MOV | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-10_POINTTYPE_TANK 14 MOV | HDS-10 | POINTTYPE | TANK 14 MOV | GDS.HDS-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-10.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-11_POINTTYPE_TANK 05 MOV | HDS-11 | POINTTYPE | TANK 05 MOV | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-11.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-11.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-12_POINTTYPE_TANK 06 MOV | HDS-12 | POINTTYPE | TANK 06 MOV | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-12.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-12.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-13_POINTTYPE_TTL PH MOV | HDS-13 | POINTTYPE | TTL PH MOV | GDS.HDS-13.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-13.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-13.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-13.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-13.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-14_POINTTYPE_TANK WAGON PH | HDS-14 | POINTTYPE | TANK WAGON PH | GDS.HDS-14.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-14.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-14.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-14.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-14.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-15_POINTTYPE_TW SIDING | HDS-15 | POINTTYPE | TW SIDING | GDS.HDS-15.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-15.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-15.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-15.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-15.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-16_OPENPATH_TANK - 03 | HDS-16 | OPENPATH | TANK - 03 | GDS.HDS-16.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-16.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-16.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-16.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-16.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-17_POINTTYPE_TANK - 04 | HDS-17 | POINTTYPE | TANK - 04 | GDS.HDS-17.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-17.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-17.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-17.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-17.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-18_OPENPATH_ETH PH MANIFOLD | HDS-18 | OPENPATH | ETH PH MANIFOLD | GDS.HDS-18.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-18.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-18.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-18.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-18.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | HDS-19_OPENPATH_ETH PH MANIFOLD | HDS-19 | OPENPATH | ETH PH MANIFOLD | GDS.HDS-19.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-19.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-19.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-19.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-19.MAINTENANCE_CALL | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1856 | Coimbatore | DYKE-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | DYKE-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | DYKE-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | DYKE-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | DYKE-05 | DRAINVALVE.DV-05.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0
1856 | Coimbatore | DYKE-06 | DRAINVALVE.DV-06.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.CAUSE_20_PCT_HCD_TF_AREA | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | Normal value | BARRIER GATE LR STATUS | Normal value
1856 | Coimbatore | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1856 | Coimbatore | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | Normal Value
1856 | Coimbatore | 1_HOOTER_FIELD_1 | 1 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1856 | Coimbatore | 2_HOOTER_FIELD_10 | 2 | HOOTER_FIELD_10 | PLC.SFTPLC.HOOTER_FIELD_10 | 0
1856 | Coimbatore | 3_HOOTER_FIELD_11 | 3 | HOOTER_FIELD_11 | PLC.SFTPLC.HOOTER_FIELD_11 | 0
1856 | Coimbatore | 4_HOOTER_FIELD_12 | 4 | HOOTER_FIELD_12 | PLC.SFTPLC.HOOTER_FIELD_12 | 0
1856 | Coimbatore | 5_HOOTER_FIELD_13 | 5 | HOOTER_FIELD_13 | PLC.SFTPLC.HOOTER_FIELD_13 | 0
1856 | Coimbatore | 6_HOOTER_FIELD_14 | 6 | HOOTER_FIELD_14 | PLC.SFTPLC.HOOTER_FIELD_14 | 0
1856 | Coimbatore | 7_HOOTER_FIELD_15 | 7 | HOOTER_FIELD_15 | PLC.SFTPLC.HOOTER_FIELD_15 | 0
1856 | Coimbatore | 8_HOOTER_FIELD_16 | 8 | HOOTER_FIELD_16 | PLC.SFTPLC.HOOTER_FIELD_16 | 0
1856 | Coimbatore | 9_HOOTER_FIELD_2 | 9 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1856 | Coimbatore | 10_HOOTER_FIELD_3 | 10 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1856 | Coimbatore | 11_HOOTER_FIELD_4 | 11 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1856 | Coimbatore | 12_HOOTER_FIELD_5 | 12 | HOOTER_FIELD_5 | PLC.SFTPLC.HOOTER_FIELD_5 | 0
1856 | Coimbatore | 13_HOOTER_FIELD_6 | 13 | HOOTER_FIELD_6 | PLC.SFTPLC.HOOTER_FIELD_6 | 0
1856 | Coimbatore | 14_HOOTER_FIELD_7 | 14 | HOOTER_FIELD_7 | PLC.SFTPLC.HOOTER_FIELD_7 | 0
1856 | Coimbatore | 15_ANY_HOOTER_FOR_HCD_FIELD | 15 | ANY_HOOTER_FOR_HCD_FIELD | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | Normal Value | ESD MAINTENANCE STATUS | Normal Value | All ROSOVs closed | Normal Value | Barrier Gate opened | Normal Value | TLF Gantry Permissive Power Off | Normal Value | All TLF Product Pumps Stopped | Normal Value | All Tanks in Dormant Mode | Normal Value | All DBBVs Closed | Normal Value | ESD Command To Process PLC | Normal Value | Siren Activated | Normal Value | ESD Hooter activated in control room | Normal Value | Power ESD Activation after 120 Sec | Normal Value
1856 | Coimbatore | ESD-01_LOCATION INCHARGE | ESD-01 | ESDPB-01 | LOCATION INCHARGE | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-02_CONTROL ROOM | ESD-02 | ESDPB-02 | CONTROL ROOM | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-03_TLF GANTRY AREA | ESD-03 | ESDPB-03 | TLF GANTRY AREA | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-04_MCC ROOM | ESD-04 | ESDPB-04 | MCC ROOM | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-05_LUBES | ESD-05 | ESDPB-05 | LUBES | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-06_SECURITY ROOM | ESD-06 | ESDPB-06 | SECURITY ROOM | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-08_TLF PMP HOUSE | ESD-08 | ESDPB-07 | TLF PMP HOUSE | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-09_NEAR TK - 01 | ESD-09 | ESDPB-08 | NEAR TK - 01 | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-10_NEAR TK - 04 | ESD-10 | ESDPB-09 | NEAR TK - 04 | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-11_NEAR TK - 16 | ESD-11 | ESDPB-10 | NEAR TK - 16 | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-12_NEAR TK - 15 | ESD-12 | ESDPB-11 | NEAR TK - 15 | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-14_CENTRAL ESD | ESD-14 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-14.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-17_WAGON SIDING - 1 | ESD-17 | ESD-17 | WAGON SIDING - 1 | ESD.ESD-17.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-19_WAGON SIDING - 2 | ESD-19 | ESD-19 | WAGON SIDING - 2 | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-20_WAGON SIDING - 3 | ESD-20 | ESD-20 | WAGON SIDING - 3 | ESD.ESD-20.ESD_STATUS | 0 | ESD.ESD-20.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-21_TANK 13 | ESD-21 | ESD-21 | TANK 13 | ESD.ESD-21.ESD_STATUS | 0 | ESD.ESD-21.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-22_INFRONT AFS CR | ESD-22 | ESD-22 | INFRONT AFS CR | ESD.ESD-22.ESD_STATUS | 0 | ESD.ESD-22.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1856 | Coimbatore | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1856 | Coimbatore | LP 01_BC-501A_BS VI MS | LP 01 | TLF | BC-501A | BS VI MS | SmartLoad-Dual.BC-501A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-501A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-501A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 02_BC-501B_BS VI HSD | LP 02 | TLF | BC-501B | BS VI HSD | SmartLoad-Dual.BC-501B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-501B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 03_BC-502A_BS VI MS | LP 03 | TLF | BC-502A | BS VI MS | SmartLoad-Dual.BC-502A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-502A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 04_BC-502B_BS VI HSD | LP 04 | TLF | BC-502B | BS VI HSD | SmartLoad-Dual.BC-502B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-502B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 05_BC-503A_BS VI MS | LP 05 | TLF | BC-503A | BS VI MS | SmartLoad-Dual.BC-503A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-503A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 06_BC-503B_BS VI HSD | LP 06 | TLF | BC-503B | BS VI HSD | SmartLoad-Dual.BC-503B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 07_BC-504A_BS VI MS | LP 07 | TLF | BC-504A | BS VI MS | SmartLoad-Dual.BC-504A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-504A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 08_BC-504B_BS VI HSD | LP 08 | TLF | BC-504B | BS VI HSD | SmartLoad-Dual.BC-504B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-504B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-504B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 09_BC-505A_BS VI MS | LP 09 | TLF | BC-505A | BS VI MS | SmartLoad-Dual.BC-505A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-505A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-505A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 10_BC-505B_BS VI HSD | LP 10 | TLF | BC-505B | BS VI HSD | SmartLoad-Dual.BC-505B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-505B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 11_BC-506A_BS VI MS | LP 11 | TLF | BC-506A | BS VI MS | SmartLoad-Dual.BC-506A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-506A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 12_BC-506B_BS VI HSD | LP 12 | TLF | BC-506B | BS VI HSD | SmartLoad-Dual.BC-506B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-506B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-506B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-506B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-506B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-506B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 13_BC-507A_BS VI MS | LP 13 | TLF | BC-507A | BS VI MS | SmartLoad-Dual.BC-507A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-507A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 14_BC-507B_BS VI HSD | LP 14 | TLF | BC-507B | BS VI HSD | SmartLoad-Dual.BC-507B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-507B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-507B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 15_BC-508A_ATF | LP 15 | TLF | BC-508A | ATF | SmartLoad-Dual.BC-508A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-508A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-508A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 16_BC-508B_ATF | LP 16 | TLF | BC-508B | ATF | SmartLoad-Dual.BC-508B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-508B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-508B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 17_BC-509A_BS VI HSD | LP 17 | TLF | BC-509A | BS VI HSD | SmartLoad-Dual.BC-509A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-509A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-509A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-509A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-509A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-509A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-509A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 18_BC-509B_BS VI HSD | LP 18 | TLF | BC-509B | BS VI HSD | SmartLoad-Dual.BC-509B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-509B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-509B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-509B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-509B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-509B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 19_BC-510A_BS VI MS | LP 19 | TLF | BC-510A | BS VI MS | SmartLoad-Dual.BC-510A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-510A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-510A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-510A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-510A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-510A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 20_BC-510B_BS VI HSD | LP 20 | TLF | BC-510B | BS VI HSD | SmartLoad-Dual.BC-510B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-510B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-510B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-510B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-510B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-510B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1856 | Coimbatore | LP 21_BC-09C_MTO | LP 21 | TLF | BC-09C | MTO | SmartLoad-Single.BC-09C.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-09C.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-09C.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-09C.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-09C.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-09C.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-09C.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-09C.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-09C.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-09C.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-09C.BATCH_STATUS | 0 | SmartLoad-Single.BC-09C.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-09C.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-09C.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1856 | Coimbatore | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1856 | Coimbatore | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-501A.PERMISSIVE_FROM_DNC_STATUS | 0
1856 | Coimbatore | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1856 | Coimbatore | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1856 | Coimbatore | WATER Level below Ref. Volume | PLC.SFTPLC.CAUSE_WATERTK_VOL_BELOW_90PCT | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1856 | Coimbatore | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1856 | Coimbatore | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1856 | Coimbatore | LRC Switch Over | CLIENT.LRC1.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1856 | Coimbatore | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.PT-02.PRESSURE |  | PressureTransmitter.PT-01.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1