## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1146 | Meerut | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED RCL | MOV.DBBV-001.OPEN_STATUS | 0 | DBBV-001 | MOV IL1 |  |  |  |  | MOV.DBBV-004.OPEN_STATUS | 0 | DBBV-004 | MOV OL | MOV.DBBV-002.OPEN_STATUS | 0 | DBBV-002 | MOV OL1 | MOV.MOV-001.OPEN_STATUS | 0 | MOV-001 | MOV RCL
1146 | Meerut | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV IL1 | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED OL | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED RCL | MOV.DBBV-005.OPEN_STATUS | 0 | DBBV-005 | MOV IL1 |  |  |  |  | MOV.DBBV-008.OPEN_STATUS | 0 | DBBV-008 | MOV OL | MOV.DBBV-006.OPEN_STATUS | 0 | DBBV-006 | MOV OL1 | MOV.MOV-002.OPEN_STATUS | 0 | MOV-002 | MOV RCL
1146 | Meerut | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED RCL | MOV.DBBV-009.OPEN_STATUS | 0 | DBBV-009 | MOV IL1 |  |  |  |  | MOV.DBBV-012.OPEN_STATUS | 0 | DBBV-012 | MOV OL | MOV.DBBV-010.OPEN_STATUS | 0 | DBBV-010 | MOV OL1 | MOV.MOV-003.OPEN_STATUS | 0 | MOV-003 | MOV RCL
1146 | Meerut | TK-04_BS VI MS | TK-04 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV IL1 | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED OL | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED RCL | MOV.DBBV-013.OPEN_STATUS | 0 | DBBV-013 | MOV IL1 |  |  |  |  | MOV.DBBV-016.OPEN_STATUS | 0 | DBBV-016 | MOV OL | MOV.DBBV-014.OPEN_STATUS | 0 | DBBV-014 | MOV OL1 | MOV.MOV-004.OPEN_STATUS | 0 | MOV-004 | MOV RCL
1146 | Meerut | TK-05_BS VI MS | TK-05 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED RCL | MOV.DBBV-017.OPEN_STATUS | 0 | DBBV-017 | MOV IL1 |  |  |  |  | MOV.DBBV-020.OPEN_STATUS | 0 | DBBV-020 | MOV OL | MOV.DBBV-018.OPEN_STATUS | 0 | DBBV-018 | MOV OL1 | MOV.MOV-005.OPEN_STATUS | 0 | MOV-005 | MOV RCL
1146 | Meerut | TK-06_BS VI MS | TK-06 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV IL1 | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED OL | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED RCL | MOV.DBBV-021.OPEN_STATUS | 0 | DBBV-021 | MOV IL1 |  |  |  |  | MOV.DBBV-024.OPEN_STATUS | 0 | DBBV-024 | MOV OL | MOV.DBBV-022.OPEN_STATUS | 0 | DBBV-022 | MOV OL1 | MOV.MOV-006.OPEN_STATUS | 0 | MOV-006 | MOV RCL
1146 | Meerut | TK-07_ETHANOL | TK-07 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED RCL | MOV.DBBV-026.OPEN_STATUS | 0 | DBBV-026 | MOV IL1 |  |  |  |  | MOV.DBBV-025.OPEN_STATUS | 0 | DBBV-025 | MOV OL |  |  |  |  | MOV.MOV-007.OPEN_STATUS | 0 | MOV-007 | MOV RCL
1146 | Meerut | TK-08_ETHANOL | TK-08 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV IL1 | MOV.ROSOV-22.FAILED_TO_CLOSE | 0 | ROSOV-22 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-23.FAILED_TO_CLOSE | 0 | ROSOV-23 | ROSOV FAILED OL | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV RCL | MOV.ROSOV-24.FAILED_TO_CLOSE | 0 | ROSOV-24 | ROSOV FAILED RCL | MOV.DBBV-029.OPEN_STATUS | 0 | DBBV-029 | MOV IL1 |  |  |  |  | MOV.DBBV-028.OPEN_STATUS | 0 | DBBV-028 | MOV OL |  |  |  |  | MOV.MOV-008.OPEN_STATUS | 0 | MOV-008 | MOV RCL
1146 | Meerut | TK-09_ETHANOL | TK-09 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | 0 | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-26.OPEN_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | 0 | ROSOV-26 | ROSOV FAILED OL | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV RCL | MOV.ROSOV-27.FAILED_TO_CLOSE | 0 | ROSOV-27 | ROSOV FAILED RCL | MOV.DBBV-031.OPEN_STATUS | 0 | DBBV-031 | MOV IL1 |  |  |  |  | MOV.DBBV-032.OPEN_STATUS | 0 | DBBV-032 | MOV OL |  |  |  |  | MOV.MOV-009.OPEN_STATUS | 0 | MOV-009 | MOV RCL
1146 | Meerut | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1146 | Meerut | TK-11_BS VI MS | TK-11 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar |  |  | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.TANK_ALERT_ALARM | 0 | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar
1146 | Meerut | TK-12_ETHANOL | TK-12 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM | 0 | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar
1146 | Meerut | TK-13_ETHANOL | TK-13 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.TANK_ALERT_ALARM | 0 | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar
1146 | Meerut | TK-14_BIO DIESEL | TK-14 | UG | BIO DIESEL | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar
1146 | Meerut | TK-16_WATER | TK-16 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar | [6 empty] | TANK.TK-16.TANK_ALERT_ALARM | 0
1146 | Meerut | TK-17_WATER | TK-17 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI_VFD | 0 | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar | [6 empty] | TANK.TK-17.TANK_ALERT_ALARM | 0

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | MOV MAINTENANCE OL1 | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1146 | Meerut_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.DBBV-001.MAINTENANCE_STATUS | 0 | DBBV-001 | MOV IL1 |  |  |  |  | MOV.MOV-001.MAINTENANCE_STATUS | 0 | MOV-001 | MOV RCL | MOV.DBBV-004.MAINTENANCE_STATUS | 0 | DBBV-004 | MOV OL | MOV.DBBV-004.MAINTENANCE_STATUS | 0 | DBBV-004 | MOV OL1
1146 | Meerut_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.DBBV-005.MAINTENANCE_STATUS | 0 | DBBV-005 | MOV IL1 |  |  |  |  | MOV.MOV-002.MAINTENANCE_STATUS | 0 | MOV-002 | MOV RCL | MOV.DBBV-008.MAINTENANCE_STATUS | 0 | DBBV-008 | MOV OL | MOV.DBBV-008.MAINTENANCE_STATUS | 0 | DBBV-008 | MOV OL1
1146 | Meerut_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.DBBV-009.MAINTENANCE_STATUS | 0 | DBBV-009 | MOV IL1 |  |  |  |  | MOV.MOV-003.MAINTENANCE_STATUS | 0 | MOV-003 | MOV RCL | MOV.DBBV-012.MAINTENANCE_STATUS | 0 | DBBV-012 | MOV OL | MOV.DBBV-012.MAINTENANCE_STATUS | 0 | DBBV-012 | MOV OL1
1146 | Meerut_M | TK-04_BS VI MS | TK-04 | AG | BS VI MS | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.DBBV-013.MAINTENANCE_STATUS | 0 | DBBV-013 | MOV IL1 |  |  |  |  | MOV.MOV-004.MAINTENANCE_STATUS | 0 | MOV-004 | MOV RCL | MOV.DBBV-016.MAINTENANCE_STATUS | 0 | DBBV-016 | MOV OL | MOV.DBBV-016.MAINTENANCE_STATUS | 0 | DBBV-016 | MOV OL1
1146 | Meerut_M | TK-05_BS VI MS | TK-05 | AG | BS VI MS | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.DBBV-017.MAINTENANCE_STATUS | 0 | DBBV-017 | MOV IL1 |  |  |  |  | MOV.MOV-005.MAINTENANCE_STATUS | 0 | MOV-005 | MOV RCL | MOV.DBBV-020.MAINTENANCE_STATUS | 0 | DBBV-020 | MOV OL | MOV.DBBV-020.MAINTENANCE_STATUS | 0 | DBBV-020 | MOV OL1
1146 | Meerut_M | TK-06_BS VI MS | TK-06 | AG | BS VI MS | TANK.TK-06.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.DBBV-021.MAINTENANCE_STATUS | 0 | DBBV-021 | MOV IL1 |  |  |  |  | MOV.MOV-006.MAINTENANCE_STATUS | 0 | MOV-006 | MOV RCL | MOV.DBBV-024.MAINTENANCE_STATUS | 0 | DBBV-024 | MOV OL | MOV.DBBV-024.MAINTENANCE_STATUS | 0 | DBBV-024 | MOV OL1
1146 | Meerut_M | TK-07_ETHANOL | TK-07 | AG | ETHANOL | TANK.TK-07.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.DBBV-026.MAINTENANCE_STATUS | 0 | DBBV-026 | MOV IL1 |  |  |  |  | MOV.MOV-007.MAINTENANCE_STATUS | 0 | MOV-007 | MOV RCL | MOV.DBBV-025.MAINTENANCE_STATUS | 0 | DBBV-025 | MOV OL | MOV.DBBV-025.MAINTENANCE_STATUS | 0 | DBBV-025 | MOV OL1
1146 | Meerut_M | TK-08_ETHANOL | TK-08 | AG | ETHANOL | TANK.TK-08.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-22.MAINTENANCE_STATUS | 0 | ROSOV-22 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-23.MAINTENANCE_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-24.MAINTENANCE_STATUS | 0 | ROSOV-24 | ROSOV RCL | MOV.DBBV-029.MAINTENANCE_STATUS | 0 | DBBV-029 | MOV IL1 |  |  |  |  | MOV.MOV-008.MAINTENANCE_STATUS | 0 | MOV-008 | MOV RCL | MOV.DBBV-028.MAINTENANCE_STATUS | 0 | DBBV-028 | MOV OL | MOV.DBBV-028.MAINTENANCE_STATUS | 0 | DBBV-028 | MOV OL1
1146 | Meerut_M | TK-09_ETHANOL | TK-09 | AG | ETHANOL | TANK.TK-09.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-25.MAINTENANCE_STATUS | 0 | ROSOV-25 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-26.MAINTENANCE_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-27.MAINTENANCE_STATUS | 0 | ROSOV-27 | ROSOV RCL | MOV.DBBV-031.MAINTENANCE_STATUS | 0 | DBBV-031 | MOV IL1 |  |  |  |  | MOV.MOV-009.MAINTENANCE_STATUS | 0 | MOV-009 | MOV RCL | MOV.DBBV-032.MAINTENANCE_STATUS | 0 | DBBV-032 | MOV OL | MOV.DBBV-032.MAINTENANCE_STATUS | 0 | DBBV-032 | MOV OL1
1146 | Meerut_M | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | TANK.TK-10.MAINTENANCE_STATUS | 0
1146 | Meerut_M | TK-11_BS VI MS | TK-11 | UG | BS VI MS | TANK.TK-11.MAINTENANCE_STATUS | 0
1146 | Meerut_M | TK-12_ETHANOL | TK-12 | UG | ETHANOL | TANK.TK-12.MAINTENANCE_STATUS | 0
1146 | Meerut_M | TK-13_ETHANOL | TK-13 | UG | ETHANOL | TANK.TK-13.MAINTENANCE_STATUS | 0
1146 | Meerut_M | TK-14_BIO DIESEL | TK-14 | UG | BIO DIESEL | TANK.TK-14.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1146 | Meerut | ADTV-PMP-01_POWERMS_DISPATCH | ADTV-PMP-01 | POWERMS | TL | DISPATCH | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-02_POWERMS_DISPATCH | ADTV-PMP-02 | POWERMS | TL | DISPATCH | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-03_TURBOHSD_DISPATCH | ADTV-PMP-03 | TURBOHSD | TL | DISPATCH | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-04_TURBOHSD_DISPATCH | ADTV-PMP-04 | TURBOHSD | TL | DISPATCH | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-05_BLUE DYE_DISPATCH | ADTV-PMP-05 | BLUE DYE | TL | DISPATCH | PUMP.ADTV-PMP-05.ON | 0 | PUMP.ADTV-PMP-05.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-05.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-06_BLUE DYE_DISPATCH | ADTV-PMP-06 | BLUE DYE | TL | DISPATCH | PUMP.ADTV-PMP-06.ON | 0 | PUMP.ADTV-PMP-06.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-06.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-07_POWER99_DISPATCH | ADTV-PMP-07 | POWER99 | TL | DISPATCH | PUMP.ADTV-PMP-07.ON | 0 | PUMP.ADTV-PMP-07.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-07.MAINTENANCE_STATUS | 0
1146 | Meerut | ADTV-PMP-08_POWER99_DISPATCH | ADTV-PMP-08 | POWER99 | TL | DISPATCH | PUMP.ADTV-PMP-08.ON | 0 | PUMP.ADTV-PMP-08.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-08.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-01_BS VI HSD_DISPATCH | PMP-01 | BS VI HSD | TL | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-02_BS VI HSD_DISPATCH | PMP-02 | BS VI HSD | TL | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-03_BS VI HSD_DISPATCH | PMP-03 | BS VI HSD | TL | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | TL | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-05_BS VI HSD_DISPATCH | PMP-05 | BS VI HSD | TL | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-06_BS VI HSD_DISPATCH | PMP-06 | BS VI HSD | TL | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-07_BS VI HSD_DISPATCH | PMP-07 | BS VI HSD | TL | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-08_BS VI MS_DISPATCH | PMP-08 | BS VI MS | TL | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-09_BS VI MS_DISPATCH | PMP-09 | BS VI MS | TL | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-10_BS VI MS_DISPATCH | PMP-10 | BS VI MS | TL | DISPATCH | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-11_BS VI MS_DISPATCH | PMP-11 | BS VI MS | TL | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-12_BS VI MS_DISPATCH | PMP-12 | BS VI MS | TL | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-13_SKO_DISPATCH | PMP-13 | SKO | TL | DISPATCH | PUMP.PMP-13.ON | 0 | PUMP.PMP-13.REMOTE_STATUS | 1 | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-14_SKO_DISPATCH | PMP-14 | SKO | TL | DISPATCH | PUMP.PMP-14.ON | 0 | PUMP.PMP-14.REMOTE_STATUS | 1 | PUMP.PMP-14.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-15_SKO_DISPATCH | PMP-15 | SKO | TL | DISPATCH | PUMP.PMP-15.ON | 0 | PUMP.PMP-15.REMOTE_STATUS | 1 | PUMP.PMP-15.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-16_ETHANOL_DISPATCH | PMP-16 | ETHANOL | TL | DISPATCH | PUMP.PMP-16.ON | 0 | PUMP.PMP-16.REMOTE_STATUS | 1 | PUMP.PMP-16.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-17_ETHANOL_DISPATCH | PMP-17 | ETHANOL | TL | DISPATCH | PUMP.PMP-17.ON | 0 | PUMP.PMP-17.REMOTE_STATUS | 1 | PUMP.PMP-17.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-18_BS VI HSD_DISPATCH | PMP-18 | BS VI HSD | TL | DISPATCH | PUMP.PMP-18.ON | 0 | PUMP.PMP-18.REMOTE_STATUS | 1 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-19_BS VI MS_DISPATCH | PMP-19 | BS VI MS | TL | DISPATCH | PUMP.PMP-19.ON | 0 | PUMP.PMP-19.REMOTE_STATUS | 1 | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-20_ETHANOL_DISPATCH | PMP-20 | ETHANOL | TL | DISPATCH | PUMP.PMP-20.ON | 0 | PUMP.PMP-20.REMOTE_STATUS | 1 | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-21_ETHANOL_DISPATCH | PMP-21 | ETHANOL | TL | DISPATCH | PUMP.PMP-21.ON | 0 | PUMP.PMP-21.REMOTE_STATUS | 1 | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-22_BIO DIESEL_DISPATCH | PMP-22 | BIO DIESEL | TL | DISPATCH | PUMP.PMP-22.ON | 0 | PUMP.PMP-22.REMOTE_STATUS | 1 | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-23_BS VI MS_DISPATCH | PMP-23 | BS VI MS | TL | DISPATCH | PUMP.PMP-23.ON | 0 | PUMP.PMP-23.REMOTE_STATUS | 1 | PUMP.PMP-23.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-24_BS VI HSD_DISPATCH | PMP-24 | BS VI HSD | WL | DISPATCH | PUMP.PMP-24.ON | 0 | PUMP.PMP-24.REMOTE_STATUS | 1 | PUMP.PMP-24.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-25_BS VI HSD_DISPATCH | PMP-25 | BS VI HSD | WL | DISPATCH | PUMP.PMP-25.ON | 0 | PUMP.PMP-25.REMOTE_STATUS | 1 | PUMP.PMP-25.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-26_BS VI HSD_DISPATCH | PMP-26 | BS VI HSD | WL | DISPATCH | PUMP.PMP-26.ON | 0 | PUMP.PMP-26.REMOTE_STATUS | 1 | PUMP.PMP-26.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-27_BS VI HSD_DISPATCH | PMP-27 | BS VI HSD | WL | DISPATCH | PUMP.PMP-27.ON | 0 | PUMP.PMP-27.REMOTE_STATUS | 1 | PUMP.PMP-27.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-28_BS VI MS_DISPATCH | PMP-28 | BS VI MS | WL | DISPATCH | PUMP.PMP-28.ON | 0 | PUMP.PMP-28.REMOTE_STATUS | 1 | PUMP.PMP-28.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-29_BS VI MS_DISPATCH | PMP-29 | BS VI MS | WL | DISPATCH | PUMP.PMP-29.ON | 0 | PUMP.PMP-29.REMOTE_STATUS | 1 | PUMP.PMP-29.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-30_BS VI MS_DISPATCH | PMP-30 | BS VI MS | WL | DISPATCH | PUMP.PMP-30.ON | 0 | PUMP.PMP-30.REMOTE_STATUS | 1 | PUMP.PMP-30.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-31_BS VI MS_DISPATCH | PMP-31 | BS VI MS | WL | DISPATCH | PUMP.PMP-31.ON | 0 | PUMP.PMP-31.REMOTE_STATUS | 1 | PUMP.PMP-31.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-32_SKO_DISPATCH | PMP-32 | SKO | WL | DISPATCH | PUMP.PMP-32.ON | 0 | PUMP.PMP-32.REMOTE_STATUS | 1 | PUMP.PMP-32.MAINTENANCE_STATUS | 0
1146 | Meerut | PMP-33_SKO_DISPATCH | PMP-33 | SKO | WL | DISPATCH | PUMP.PMP-33.ON | 0 | PUMP.PMP-33.REMOTE_STATUS | 1 | PUMP.PMP-33.MAINTENANCE_STATUS | 0
1146 | Meerut | VRU-PMP-01_BS VI HSD_Both | VRU-PMP-01 | BS VI HSD | Both | Both | PUMP.VRU-PMP-01.ON | 0 |  | 1
1146 | Meerut | VRU-PMP-02_BS VI HSD_Both | VRU-PMP-02 | BS VI HSD | Both | Both | PUMP.VRU-PMP-02.ON | 0 |  | 1

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP FAIL TO START STANDBY1 | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1146 | Meerut | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1146 | Meerut | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1146 | Meerut | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1146 | Meerut | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0
1146 | Meerut | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0
1146 | Meerut | Farthest Point PT_WATER Pressure_Near Tank no. 01 | Farthest Point PT | WATER Pressure | PT | Near Tank no. 01 |  |  |  |  | PressureTransmitter.FPT-01.MAINTENANCE_STATUS | 0
1146 | Meerut | Nearest Point PT_WATER Pressure_FWP pump house | Nearest Point PT | WATER Pressure | PT | FWP pump house |  |  |  |  | PressureTransmitter.FPT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1146 | Meerut | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.LOAD_ON_UPS | 0 | UPS.UPS-01.MAIN_AC_FAIL | 0
1146 | Meerut | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.LOAD_ON_UPS | 0 | UPS.UPS-02.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1146 | Meerut | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1146 | Meerut | SFT PLC_Safety PLC | SFT PLC | Safety PLC

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1146 | Meerut | HCD-01_OPEN_TTL PUMP HOUSE | HCD-01 | OPEN | TTL PUMP HOUSE | GDS.HCD-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-01.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-02_OPEN_TWD PUMP HOUSE | HCD-02 | OPEN | TWD PUMP HOUSE | GDS.HCD-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-02.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-03_FIXE_TTL PUMP HOUSE | HCD-03 | FIXE | TTL PUMP HOUSE | GDS.HCD-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-03.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-04_FIXE_TWD PUMP HOUSE | HCD-04 | FIXE | TWD PUMP HOUSE | GDS.HCD-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-04.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-05_OPEN_TANKFARM TK-6 MS | HCD-05 | OPEN | TANKFARM TK-6 MS | GDS.HCD-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-05.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-06_OPEN_TANKFARM TK-5 MS | HCD-06 | OPEN | TANKFARM TK-5 MS | GDS.HCD-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-06.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-07_FIXE_TANKFARM TK-9 ETH | HCD-07 | FIXE | TANKFARM TK-9 ETH | GDS.HCD-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-07.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-08_FIXE_ETP ROOM | HCD-08 | FIXE | ETP ROOM | GDS.HCD-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-08.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-09_FIXE_VRU ROOM | HCD-09 | FIXE | VRU ROOM | GDS.HCD-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-09.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HCD-10_OPEN_TTL PUMP HOUSE | HCD-10 | OPEN | TTL PUMP HOUSE | GDS.HCD-10.HYDROCARBON_40_PCT_LEL |  | GDS.HCD-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-10.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1146 | Meerut | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1146 | Meerut | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1146 | Meerut | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1146 | Meerut | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1146 | Meerut | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1146 | Meerut | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1146 | Meerut | HOOTER1_HOOTER_FIELD_1 | HOOTER1 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1146 | Meerut | HOOTER2_HOOTER_FIELD_2 | HOOTER2 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1146 | Meerut | HOOTER3_HOOTER_FIELD_3 | HOOTER3 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1146 | Meerut | HOOTER4_HOOTER_FIELD_4 | HOOTER4 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1146 | Meerut | HOOTER5_HOOTER_FOR_ESD_CR | HOOTER5 | HOOTER_FOR_ESD_CR | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1146 | Meerut | HOOTER6_HOOTER_FOR_HC_CR | HOOTER6 | HOOTER_FOR_HC_CR | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1146 | Meerut | HOOTER7_HOOTER_FOR_RIMSEAL_CR | HOOTER7 | HOOTER_FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1146 | Meerut | ESD-01_ESD PB TLF G-1 BAY-4 CATWALK | ESD-01 | ESD_PB_01 | ESD PB TLF G-1 BAY-4 CATWALK | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-02_ESD PB AT TLF G-1 BAY-3 | ESD-02 | ESD_PB_02 | ESD PB AT TLF G-1 BAY-3 | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-03_ESD PB TLF G-2 BAY-12 CATWALK | ESD-03 | ESD_PB_03 | ESD PB TLF G-2 BAY-12 CATWALK | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-04_ESD PB AT TLF G-2 BAY-11 | ESD-04 | ESD_PB_04 | ESD PB AT TLF G-2 BAY-11 | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-05_ESD PB AT TANK-09 | ESD-05 | ESD_PB_05 | ESD PB AT TANK-09 | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-06_ESD PB AT TANK-04 | ESD-06 | ESD_PB_06 | ESD PB AT TANK-04 | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-07_ESD PB AT TANK-01 | ESD-07 | ESD_PB_07 | ESD PB AT TANK-01 | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-08_ESD PB AT TANK-03 | ESD-08 | ESD_PB_08 | ESD PB AT TANK-03 | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-09_ESD PB AT VRU | ESD-09 | ESD_PB_09 | ESD PB AT VRU | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-10_ESD PB AT RLY SIDING | ESD-10 | ESD_PB_10 | ESD PB AT RLY SIDING | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-11_SIDING ESD PB1 | ESD-11 | ESD_PB_11 | SIDING ESD PB1 | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-12_ESD PB AT TLF PUMP | ESD-12 | ESD_PB_12 | ESD PB AT TLF PUMP | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-13_ESD PB AT TWD pump | ESD-13 | ESD_PB_13 | ESD PB AT TWD pump | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-14_SIDING ESD PB2 | ESD-14 | ESD_PB_14 | SIDING ESD PB2 | ESD.ESD-14.ESD_STATUS | 0 | ESD.ESD-14.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-15_SIDING ESD PB3 | ESD-15 | ESD_PB_15 | SIDING ESD PB3 | ESD.ESD-15.ESD_STATUS | 0 | ESD.ESD-15.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-16_ESD PB AT SECURITY ROOM | ESD-16 | ESD_PB_16 | ESD PB AT SECURITY ROOM | ESD.ESD-16.ESD_STATUS | 0 | ESD.ESD-16.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-17_ESD PB AT OFFICE BUILDING | ESD-17 | ESD_PB_17 | ESD PB AT OFFICE BUILDING | ESD.ESD-17.ESD_STATUS | 0 | ESD.ESD-17.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-18_ESD PB AT TM ROOM | ESD-18 | ESD_PB_18 | ESD PB AT TM ROOM | ESD.ESD-18.ESD_STATUS | 0 | ESD.ESD-18.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-19_ESD PB AT MCC ROOM | ESD-19 | ESD_PB_19 | ESD PB AT MCC ROOM | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-20_ESD PB AT CONTROL ROOM | ESD-20 | ESD_PB_20 | ESD PB AT CONTROL ROOM | ESD.ESD-20.ESD_STATUS | 0 | ESD.ESD-20.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-30_EPB TO PUMP FROM GANTRY-2 PUSH BUTTON | ESD-30 | ESD_PB_BIO_509 | EPB TO PUMP FROM GANTRY-2 PUSH BUTTON | ESD.ESD-30.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-36_CENTRAL ESD | ESD-36 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-36.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-40_ESD PB AT ETP | ESD-40 | ESD_PB_21 | ESD PB AT ETP | ESD.ESD-40.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-41_ESD ETP-21 | ESD-41 | ESD_ETP_21 | ESD ETP-21 | ESD.ESD-41.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1146 | Meerut | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1146 | Meerut | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 02_BC-01B_BS VI MS | LP 02 | TLF | BC-01B | BS VI MS | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 03_BC-02A_BS VI HSD | LP 03 | TLF | BC-02A | BS VI HSD | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 04_BC-02B_BS VI HSD | LP 04 | TLF | BC-02B | BS VI HSD | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 05_BC-03A_BS VI HSD | LP 05 | TLF | BC-03A | BS VI HSD | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 07_BC-04A_BS VI MS | LP 07 | TLF | BC-04A | BS VI MS | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 09_BC-05A_BS VI MS | LP 09 | TLF | BC-05A | BS VI MS | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 11_BC-06A_BS VI MS | LP 11 | TLF | BC-06A | BS VI MS | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 13_BC-07A_BS VI MS | LP 13 | TLF | BC-07A | BS VI MS | SmartLoad-Dual.BC-07A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 14_BC-07B_BS VI HSD | LP 14 | TLF | BC-07B | BS VI HSD | SmartLoad-Dual.BC-07B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-07B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 15_BC-08A_BS VI MS | LP 15 | TLF | BC-08A | BS VI MS | SmartLoad-Dual.BC-08A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-08A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 16_BC-08B_BS VI HSD | LP 16 | TLF | BC-08B | BS VI HSD | SmartLoad-Dual.BC-08B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-08B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 17_BC-09A_BS VI HSD | LP 17 | TLF | BC-09A | BS VI HSD | SmartLoad-Dual.BC-09A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-09A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-09A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-09A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-09A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 18_BC-09B_BS VI HSD | LP 18 | TLF | BC-09B | BS VI HSD | SmartLoad-Dual.BC-09B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-09B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 19_BC-10A_BS VI HSD | LP 19 | TLF | BC-10A | BS VI HSD | SmartLoad-Dual.BC-10A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-10A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-10A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 20_BC-10B_BS VI HSD | LP 20 | TLF | BC-10B | BS VI HSD | SmartLoad-Dual.BC-10B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-10B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 21_BC-11A_BS VI HSD | LP 21 | TLF | BC-11A | BS VI HSD | SmartLoad-Dual.BC-11A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-11A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 22_BC-11B_BS VI HSD | LP 22 | TLF | BC-11B | BS VI HSD | SmartLoad-Dual.BC-11B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-11B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 23_BC-12A_BS VI MS | LP 23 | TLF | BC-12A | BS VI MS | SmartLoad-Dual.BC-12A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-12A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 24_BC-12B_BS VI HSD | LP 24 | TLF | BC-12B | BS VI HSD | SmartLoad-Dual.BC-12B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-12B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 25_BC-13A_BS VI MS | LP 25 | TLF | BC-13A | BS VI MS | SmartLoad-Dual.BC-13A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 26_BC-13B_BS VI HSD | LP 26 | TLF | BC-13B | BS VI HSD | SmartLoad-Dual.BC-13B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 27_BC-14A_BS VI MS | LP 27 | TLF | BC-14A | BS VI MS | SmartLoad-Dual.BC-14A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 28_BC-14B_BS VI HSD | LP 28 | TLF | BC-14B | BS VI HSD | SmartLoad-Dual.BC-14B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 29_BC-15A_BS VI MS | LP 29 | TLF | BC-15A | BS VI MS | SmartLoad-Dual.BC-15A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 30_BC-15B_BS VI HSD | LP 30 | TLF | BC-15B | BS VI HSD | SmartLoad-Dual.BC-15B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-15B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 31_BC-16A_BS VI MS | LP 31 | TLF | BC-16A | BS VI MS | SmartLoad-Dual.BC-16A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-16A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-16A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-16A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-16A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-16A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-16A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1146 | Meerut | LP 32_BC-16B_BS VI HSD | LP 32 | TLF | BC-16B | BS VI HSD | SmartLoad-Dual.BC-16B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-16B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1146 | Meerut | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1146 | Meerut | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1146 | Meerut | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1146 | Meerut | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1146 | Meerut | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1146 | Meerut | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1146 | Meerut | Gantry Permissive Off |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1146 | Meerut | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1146 | Meerut | Operability Index | PUMP.FWP-01.ON | 0 | PUMP.FWP-02.ON | 0 | PUMP.FWP-03.ON | 0 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.FPT-02.PRESSURE |  | PressureTransmitter.FPT-01.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1