## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH HIGH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1221 | Delhi | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-201.OPEN_STATUS | 0 | ROSOV-201 | ROSOV IL1 | MOV.ROSOV-201.FAILED_TO_CLOSE | 0 | ROSOV-201 | ROSOV FAILED IL1 | MOV.ROSOV-202.OPEN_STATUS | 0 | ROSOV-202 | ROSOV IL2 | MOV.ROSOV-202.FAILED_TO_CLOSE | 0 | ROSOV-202 | ROSOV FAILED IL2 | [16 empty] | MOV.MOV-201.OPEN_STATUS | 0 | MOV-201 | MOV IL1 |  |  |  |  | MOV.MOV-202.OPEN_STATUS | 0 | MOV-202 | MOV OL | MOV.MOV-203.OPEN_STATUS | 0 | MOV-203 | MOV RCL
1221 | Delhi | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-203.OPEN_STATUS | 0 | ROSOV-203 | ROSOV IL1 | MOV.ROSOV-203.FAILED_TO_CLOSE | 0 | ROSOV-203 | ROSOV FAILED IL1 | MOV.ROSOV-204.OPEN_STATUS | 0 | ROSOV-204 | ROSOV IL2 | MOV.ROSOV-204.FAILED_TO_CLOSE | 0 | ROSOV-204 | ROSOV FAILED IL2 | [16 empty] | MOV.MOV-204.OPEN_STATUS | 0 | MOV-204 | MOV IL1 |  |  |  |  | MOV.MOV-205.OPEN_STATUS | 0 | MOV-205 | MOV OL | MOV.MOV-206.OPEN_STATUS | 0 | MOV-206 | MOV RCL
1221 | Delhi | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-205.OPEN_STATUS | 0 | ROSOV-205 | ROSOV IL1 | MOV.ROSOV-205.FAILED_TO_CLOSE | 0 | ROSOV-205 | ROSOV FAILED IL1 | MOV.ROSOV-206.OPEN_STATUS | 0 | ROSOV-206 | ROSOV IL2 | MOV.ROSOV-206.FAILED_TO_CLOSE | 0 | ROSOV-206 | ROSOV FAILED IL2 | [16 empty] | MOV.MOV-207.OPEN_STATUS | 0 | MOV-207 | MOV IL1 |  |  |  |  | MOV.MOV-208.OPEN_STATUS | 0 | MOV-208 | MOV OL | MOV.MOV-209.OPEN_STATUS | 0 | MOV-209 | MOV RCL
1221 | Delhi | TK-04_ETHANOL | TK-04 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-302.OPEN_STATUS | 0 | ROSOV-302 | ROSOV IL1 | MOV.ROSOV-302.FAILED_TO_CLOSE | 0 | ROSOV-302 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-301.OPEN_STATUS | 0 | ROSOV-301 | ROSOV OL | MOV.ROSOV-301.FAILED_TO_CLOSE | 0 | ROSOV-301 | ROSOV FAILED OL | [8 empty] | MOV.MOV-301.OPEN_STATUS | 0 | MOV-301 | MOV IL1 |  |  |  |  | MOV.MOV-302.OPEN_STATUS | 0 | MOV-302 | MOV OL
1221 | Delhi | TK-05_ETHANOL | TK-05 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-304.OPEN_STATUS | 0 | ROSOV-304 | ROSOV IL1 | MOV.ROSOV-304.FAILED_TO_CLOSE | 0 | ROSOV-304 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-303.OPEN_STATUS | 0 | ROSOV-303 | ROSOV OL | MOV.ROSOV-303.FAILED_TO_CLOSE | 0 | ROSOV-303 | ROSOV FAILED OL | [8 empty] | MOV.MOV-304.OPEN_STATUS | 0 | MOV-304 | MOV IL1 |  |  |  |  | MOV.MOV-305.OPEN_STATUS | 0 | MOV-305 | MOV OL
1221 | Delhi | TK-06_BS VI MS | TK-06 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-101.OPEN_STATUS | 0 | ROSOV-101 | ROSOV IL1 | MOV.ROSOV-101.FAILED_TO_CLOSE | 0 | ROSOV-101 | ROSOV FAILED IL1 | MOV.ROSOV-102.OPEN_STATUS | 0 | ROSOV-102 | ROSOV IL2 | MOV.ROSOV-102.FAILED_TO_CLOSE | 0 | ROSOV-102 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-103.OPEN_STATUS | 0 | ROSOV-103 | ROSOV RCL | MOV.ROSOV-103.FAILED_TO_CLOSE | 0 | ROSOV-103 | ROSOV FAILED RCL | MOV.MOV-101.OPEN_STATUS | 0 | MOV-101 | MOV IL1 |  |  |  |  | MOV.MOV-102.OPEN_STATUS | 0 | MOV-102 | MOV OL | MOV.MOV-103.OPEN_STATUS | 0 | MOV-103 | MOV RCL
1221 | Delhi | TK-07_BS VI MS | TK-07 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-104.OPEN_STATUS | 0 | ROSOV-104 | ROSOV IL1 | MOV.ROSOV-104.FAILED_TO_CLOSE | 0 | ROSOV-104 | ROSOV FAILED IL1 | MOV.ROSOV-105.OPEN_STATUS | 0 | ROSOV-105 | ROSOV IL2 | MOV.ROSOV-105.FAILED_TO_CLOSE | 0 | ROSOV-105 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-106.OPEN_STATUS | 0 | ROSOV-106 | ROSOV RCL | MOV.ROSOV-106.FAILED_TO_CLOSE | 0 | ROSOV-106 | ROSOV FAILED RCL | MOV.MOV-104.OPEN_STATUS | 0 | MOV-104 | MOV IL1 |  |  |  |  | MOV.MOV-105.OPEN_STATUS | 0 | MOV-105 | MOV OL | MOV.MOV-106.OPEN_STATUS | 0 | MOV-106 | MOV RCL
1221 | Delhi | TK-08_BS VI MS | TK-08 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-107.OPEN_STATUS | 0 | ROSOV-107 | ROSOV IL1 | MOV.ROSOV-107.FAILED_TO_CLOSE | 0 | ROSOV-107 | ROSOV FAILED IL1 | MOV.ROSOV-108.OPEN_STATUS | 0 | ROSOV-108 | ROSOV IL2 | MOV.ROSOV-108.FAILED_TO_CLOSE | 0 | ROSOV-108 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-109.OPEN_STATUS | 0 | ROSOV-109 | ROSOV RCL | MOV.ROSOV-109.FAILED_TO_CLOSE | 0 | ROSOV-109 | ROSOV FAILED RCL | MOV.MOV-107.OPEN_STATUS | 0 | MOV-107 | MOV IL1 |  |  |  |  | MOV.MOV-108.OPEN_STATUS | 0 | MOV-108 | MOV OL | MOV.MOV-109.OPEN_STATUS | 0 | MOV-109 | MOV RCL
1221 | Delhi | TK-09_ETHANOL | TK-09 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-402.OPEN_STATUS | 0 | ROSOV-402 | ROSOV IL1 | MOV.ROSOV-402.FAILED_TO_CLOSE | 0 | ROSOV-402 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-401.OPEN_STATUS | 0 | ROSOV-401 | ROSOV OL | MOV.ROSOV-401.FAILED_TO_CLOSE | 0 | ROSOV-401 | ROSOV FAILED OL | [8 empty] | MOV.MOV-401.OPEN_STATUS | 0 | MOV-401 | MOV IL1 |  |  |  |  | MOV.MOV-402.OPEN_STATUS | 0 | MOV-402 | MOV OL
1221 | Delhi | TK-10_ETHANOL | TK-10 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-404.OPEN_STATUS | 0 | ROSOV-404 | ROSOV IL1 | MOV.ROSOV-404.FAILED_TO_CLOSE | 0 | ROSOV-404 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-403.OPEN_STATUS | 0 | ROSOV-403 | ROSOV OL | MOV.ROSOV-403.FAILED_TO_CLOSE | 0 | ROSOV-403 | ROSOV FAILED OL | [8 empty] | MOV.MOV-403.OPEN_STATUS | 0 | MOV-403 | MOV IL1 |  |  |  |  | MOV.MOV-404.OPEN_STATUS | 0 | MOV-404 | MOV OL
1221 | Delhi | TK-11_SOLVANT | TK-11 | AG | SOLVANT | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar |  |  | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.TANK_ALERT_ALARM | 0 | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar
1221 | Delhi | TK-12_BS VI HSD | TK-12 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM | 0 | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar
1221 | Delhi | TK-13_SOLVANT | TK-13 | AG | SOLVANT | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.TANK_ALERT_ALARM | 0 | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar
1221 | Delhi | TK-14_BS VI MS | TK-14 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar
1221 | Delhi | TK-15_MTO | TK-15 | AG | MTO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar
1221 | Delhi | TK-16_ETHANOL | TK-16 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar |  |  | TANK.TK-16.HIGH_LEVEL | 0 | TK-16 | Primary Radar | TANK.TK-16.TANK_ALERT_ALARM | 0 | TANK.TK-16.HIGH_HIGH_LEVEL | 0 | TK-16 | Primary Radar
1221 | Delhi | TK-17_BS VI HSD | TK-17 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar | [6 empty] | TANK.TK-17.TANK_ALERT_ALARM | 0
1221 | Delhi | TK-18_WATER | TK-18 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-18.LEVEL |  | TK-18 | Primary Radar
1221 | Delhi | TK-19_WATER | TK-19 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-19.LEVEL |  | TK-19 | Primary Radar
1221 | Delhi | TK-20_WATER | TK-20 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-20.LEVEL |  | TK-20 | Primary Radar
1221 | Delhi | TK-23_BIOHSD | TK-23 | AG | BIOHSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-23.LEVEL |  | TK-23 | Primary Radar
1221 | Delhi | TK-24_BIOHSD | TK-24 | AG | BIOHSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-24.LEVEL |  | TK-24 | Primary Radar
1221 | Delhi | TK-25_BIOHSD | TK-25 | AG | BIOHSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-25.LEVEL |  | TK-25 | Primary Radar
1221 | Delhi | TK-26_BIOHSD | TK-26 | AG | BIOHSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-26.LEVEL |  | TK-26 | Primary Radar

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1221 | Delhi_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-201.MAINTENANCE_STATUS | 0 | ROSOV-201 | ROSOV IL1 | MOV.ROSOV-202.MAINTENANCE_STATUS | 0 | ROSOV-202 | ROSOV IL2 | [8 empty] | MOV.MOV-201.MAINTENANCE_STATUS | 0 | MOV-201 | MOV IL1 |  |  |  |  | MOV.MOV-203.MAINTENANCE_STATUS | 0 | MOV-203 | MOV RCL | MOV.MOV-202.MAINTENANCE_STATUS | 0 | MOV-202 | MOV OL
1221 | Delhi_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-203.MAINTENANCE_STATUS | 0 | ROSOV-203 | ROSOV IL1 | MOV.ROSOV-204.MAINTENANCE_STATUS | 0 | ROSOV-204 | ROSOV IL2 | [8 empty] | MOV.MOV-204.MAINTENANCE_STATUS | 0 | MOV-204 | MOV IL1 |  |  |  |  | MOV.MOV-206.MAINTENANCE_STATUS | 0 | MOV-206 | MOV RCL | MOV.MOV-205.MAINTENANCE_STATUS | 0 | MOV-205 | MOV OL
1221 | Delhi_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-205.MAINTENANCE_STATUS | 0 | ROSOV-205 | ROSOV IL1 | MOV.ROSOV-206.MAINTENANCE_STATUS | 0 | ROSOV-206 | ROSOV IL2 | [8 empty] | MOV.MOV-207.MAINTENANCE_STATUS | 0 | MOV-207 | MOV IL1 |  |  |  |  | MOV.MOV-209.MAINTENANCE_STATUS | 0 | MOV-209 | MOV RCL | MOV.MOV-208.MAINTENANCE_STATUS | 0 | MOV-208 | MOV OL
1221 | Delhi_M | TK-04_ETHANOL | TK-04 | AG | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-302.MAINTENANCE_STATUS | 0 | ROSOV-302 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-301.MAINTENANCE_STATUS | 0 | ROSOV-301 | ROSOV OL |  |  |  |  | MOV.MOV-301.MAINTENANCE_STATUS | 0 | MOV-301 | MOV IL1 | [8 empty] | MOV.MOV-302.MAINTENANCE_STATUS | 0 | MOV-302 | MOV OL
1221 | Delhi_M | TK-05_ETHANOL | TK-05 | AG | ETHANOL | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-304.MAINTENANCE_STATUS | 0 | ROSOV-304 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-303.MAINTENANCE_STATUS | 0 | ROSOV-303 | ROSOV OL |  |  |  |  | MOV.MOV-304.MAINTENANCE_STATUS | 0 | MOV-304 | MOV IL1 | [8 empty] | MOV.MOV-305.MAINTENANCE_STATUS | 0 | MOV-305 | MOV OL
1221 | Delhi_M | TK-06_BS VI MS | TK-06 | AG | BS VI MS | TANK.TK-06.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-101.MAINTENANCE_STATUS | 0 | ROSOV-101 | ROSOV IL1 | MOV.ROSOV-102.MAINTENANCE_STATUS | 0 | ROSOV-102 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-103.MAINTENANCE_STATUS | 0 | ROSOV-103 | ROSOV RCL | MOV.MOV-101.MAINTENANCE_STATUS | 0 | MOV-101 | MOV IL1 |  |  |  |  | MOV.MOV-103.MAINTENANCE_STATUS | 0 | MOV-103 | MOV RCL | MOV.MOV-102.MAINTENANCE_STATUS | 0 | MOV-102 | MOV OL
1221 | Delhi_M | TK-07_BS VI MS | TK-07 | AG | BS VI MS | TANK.TK-07.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-104.MAINTENANCE_STATUS | 0 | ROSOV-104 | ROSOV IL1 | MOV.ROSOV-105.MAINTENANCE_STATUS | 0 | ROSOV-105 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-106.MAINTENANCE_STATUS | 0 | ROSOV-106 | ROSOV RCL | MOV.MOV-104.MAINTENANCE_STATUS | 0 | MOV-104 | MOV IL1 |  |  |  |  | MOV.MOV-106.MAINTENANCE_STATUS | 0 | MOV-106 | MOV RCL | MOV.MOV-105.MAINTENANCE_STATUS | 0 | MOV-105 | MOV OL
1221 | Delhi_M | TK-08_BS VI MS | TK-08 | AG | BS VI MS | TANK.TK-08.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-107.MAINTENANCE_STATUS | 0 | ROSOV-107 | ROSOV IL1 | MOV.ROSOV-108.MAINTENANCE_STATUS | 0 | ROSOV-108 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-109.MAINTENANCE_STATUS | 0 | ROSOV-109 | ROSOV RCL | MOV.MOV-107.MAINTENANCE_STATUS | 0 | MOV-107 | MOV IL1 |  |  |  |  | MOV.MOV-109.MAINTENANCE_STATUS | 0 | MOV-109 | MOV RCL | MOV.MOV-108.MAINTENANCE_STATUS | 0 | MOV-108 | MOV OL
1221 | Delhi_M | TK-09_ETHANOL | TK-09 | AG | ETHANOL | TANK.TK-09.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-402.MAINTENANCE_STATUS | 0 | ROSOV-402 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-401.MAINTENANCE_STATUS | 0 | ROSOV-401 | ROSOV OL |  |  |  |  | MOV.MOV-401.MAINTENANCE_STATUS | 0 | MOV-401 | MOV IL1 | [8 empty] | MOV.MOV-402.MAINTENANCE_STATUS | 0 | MOV-402 | MOV OL
1221 | Delhi_M | TK-10_ETHANOL | TK-10 | AG | ETHANOL | TANK.TK-10.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | MOV.ROSOV-404.MAINTENANCE_STATUS | 0 | ROSOV-404 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-403.MAINTENANCE_STATUS | 0 | ROSOV-403 | ROSOV OL |  |  |  |  | MOV.MOV-403.MAINTENANCE_STATUS | 0 | MOV-403 | MOV IL1 | [8 empty] | MOV.MOV-404.MAINTENANCE_STATUS | 0 | MOV-404 | MOV OL
1221 | Delhi_M | TK-11_SOLVANT | TK-11 | AG | SOLVANT | TANK.TK-11.MAINTENANCE_STATUS | 0
1221 | Delhi_M | TK-12_BS VI HSD | TK-12 | AG | BS VI HSD | TANK.TK-12.MAINTENANCE_STATUS | 0
1221 | Delhi_M | TK-13_SOLVANT | TK-13 | AG | SOLVANT | TANK.TK-13.MAINTENANCE_STATUS | 0
1221 | Delhi_M | TK-14_BS VI MS | TK-14 | AG | BS VI MS | TANK.TK-14.MAINTENANCE_STATUS | 0
1221 | Delhi_M | TK-15_MTO | TK-15 | AG | MTO | TANK.TK-15.MAINTENANCE_STATUS | 0
1221 | Delhi_M | TK-16_ETHANOL | TK-16 | AG | ETHANOL | TANK.TK-16.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1221 | Delhi | ADTV-PMP-01_POWERMS_DISPATCH | ADTV-PMP-01 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1221 | Delhi | ADTV-PMP-02_POWERMS_DISPATCH | ADTV-PMP-02 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1221 | Delhi | ADTV-PMP-03_POWERMS_DISPATCH | ADTV-PMP-03 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1221 | Delhi | ADTV-PMP-04_POWERMS_DISPATCH | ADTV-PMP-04 | POWERMS | Truck Loading | DISPATCH | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1221 | Delhi | ADTV-PMP-05_TURBOHSD_DISPATCH | ADTV-PMP-05 | TURBOHSD | Truck Loading | DISPATCH | PUMP.ADTV-PMP-05.ON | 0 | PUMP.ADTV-PMP-05.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-05.MAINTENANCE_STATUS | 0
1221 | Delhi | ADTV-PMP-06_TURBOHSD_DISPATCH | ADTV-PMP-06 | TURBOHSD | Truck Loading | DISPATCH | PUMP.ADTV-PMP-06.ON | 0 | PUMP.ADTV-PMP-06.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-06.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-01_BS VI HSD_DISPATCH | PMP-01 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-02_BS VI HSD_DISPATCH | PMP-02 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-03_BS VI HSD_DISPATCH | PMP-03 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-05_BS VI MS_DISPATCH | PMP-05 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-06_BS VI MS_DISPATCH | PMP-06 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-07_BS VI MS_DISPATCH | PMP-07 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-08_BS VI MS_DISPATCH | PMP-08 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-09_ETHANOL_DISPATCH | PMP-09 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-10_ETHANOL_DISPATCH | PMP-10 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-11_ETHANOL_DISPATCH | PMP-11 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-12_ETHANOL_DISPATCH | PMP-12 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-13_ETHANOL_DISPATCH | PMP-13 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-13.ON | 0 | PUMP.PMP-13.REMOTE_STATUS | 1 | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-12_BS VI HSD_DISPATCH | PMP-VT-12 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-VT-12.ON | 0 | PUMP.PMP-VT-12.REMOTE_STATUS | 1 | PUMP.PMP-VT-12.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-14_BS VI MS_DISPATCH | PMP-VT-14 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-VT-14.ON | 0 | PUMP.PMP-VT-14.REMOTE_STATUS | 1 | PUMP.PMP-VT-14.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-15_ETHANOL_DISPATCH | PMP-VT-15 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-VT-15.ON | 0 | PUMP.PMP-VT-15.REMOTE_STATUS | 1 | PUMP.PMP-VT-15.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-16_ETHANOL_DISPATCH | PMP-VT-16 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-VT-16.ON | 0 | PUMP.PMP-VT-16.REMOTE_STATUS | 1 | PUMP.PMP-VT-16.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-23_BIO DIESEL_DISPATCH | PMP-VT-23 | BIO DIESEL | Truck Loading | DISPATCH | PUMP.PMP-VT-23.ON | 0 | PUMP.PMP-VT-23.REMOTE_STATUS | 1 | PUMP.PMP-VT-23.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-25_BIO DIESEL_DISPATCH | PMP-VT-25 | BIO DIESEL | Truck Loading | DISPATCH | PUMP.PMP-VT-25.ON | 0 | PUMP.PMP-VT-25.REMOTE_STATUS | 1 | PUMP.PMP-VT-25.MAINTENANCE_STATUS | 0
1221 | Delhi | PMP-VT-26_BIO DIESEL_DISPATCH | PMP-VT-26 | BIO DIESEL | Truck Loading | DISPATCH | PUMP.PMP-VT-26.ON | 0 | PUMP.PMP-VT-26.REMOTE_STATUS | 1 | PUMP.PMP-VT-26.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction | PUMP ON STATUS | Normal value | PUMP LR STATUS | Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | Normal value | FIRE PUMP FAIL TO START 2 | Normal value | FIRE PUMP FAIL TO START 3 | Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP FAIL TO START STANDBY1 | Normal value | FIRE PUMP FAIL TO START STANDBY2 | Normal value | FIRE PUMP TRIPPED FAULT | Normal value | FIRE PUMP LLOP ALARM | Normal value | FIRE PUMP HWT ALARM | Normal value
1221 | Delhi | FWP-01_Water_DISPATCH | FWP-01 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN3 | 0 | PUMP.JCY-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0
1221 | Delhi | FWP-02_Water_DISPATCH | FWP-02 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN3 | 0 | PUMP.JCY-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0
1221 | Delhi | FWP-03_Water_DISPATCH | FWP-03 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN3 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-03.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0
1221 | Delhi | FWP-04_Water_DISPATCH | FWP-04 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-04.ON | 0 | PUMP.FWP-04.REMOTE_STATUS | 1 | PUMP.FWP-04.MAINTENANCE_STATUS | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN3 | 0 |  |  | PUMP.FWP-04.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-04.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-04.PUMP_TRIPPED | 0
1221 | Delhi | FWP-05_Water_DISPATCH | FWP-05 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-05.ON | 0 | PUMP.FWP-05.REMOTE_STATUS | 1 | PUMP.FWP-05.MAINTENANCE_STATUS | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN3 | 0 |  |  | PUMP.FWP-05.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-05.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-05.PUMP_TRIPPED | 0
1221 | Delhi | JCY-01_Water_DISPATCH | JCY-01 | Water | PUMP HOUSE | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 | [10 empty] | PUMP.JCY-01.PUMP_TRIPPED | 0
1221 | Delhi | JCY-02_Water_DISPATCH | JCY-02 | Water | PUMP HOUSE | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 | [10 empty] | PUMP.JCY-02.PUMP_TRIPPED | 0
1221 | Delhi | Farthest Point PT_WP_DISPATCH | Farthest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.FPT-01.MAINTENANCE_STATUS | 0
1221 | Delhi | Nearest Point PT_WP_DISPATCH | Nearest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.FPT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | Normal Value | LOW BATTERY | Normal Value | UPS ON | Normal Value | UPS MAIN AC FAIL | Normal Value
1221 | Delhi | UPS-01_Control Room | UPS-01 | Control Room
1221 | Delhi | UPS-02_Control Room | UPS-02 | Control Room

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1221 | Delhi | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1221 | Delhi | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB | [8 empty] | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | Normal Value | HCD 20 % ALARM | Normal Value | HCD FAULT | Normal Value | MISALIGNMENT FAULT | Normal Value | HCD MAINTENANCE | Normal Value | HCD Hooter Activated | Normal value
1221 | Delhi | HCD-01_OPEN PATH_HCD-01 TLF PUMP HOUSE | HCD-01 | OPEN PATH | HCD-01 TLF PUMP HOUSE | GDS.HCD-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-01.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-02_OPEN PATH_HCD-02 | HCD-02 | OPEN PATH | HCD-02 | GDS.HCD-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-02.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-03_OPEN PATH_HCD-03 | HCD-03 | OPEN PATH | HCD-03 | GDS.HCD-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-03.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-04_POINT TYPE_HCD-04 | HCD-04 | POINT TYPE | HCD-04 | GDS.HCD-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-04.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-05_OPEN PATH_HCD-05 | HCD-05 | OPEN PATH | HCD-05 | GDS.HCD-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-05.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-06_POINT TYPE_HCD-06 | HCD-06 | POINT TYPE | HCD-06 | GDS.HCD-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-06.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-07_POINT TYPE_HCD-07 | HCD-07 | POINT TYPE | HCD-07 | GDS.HCD-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-07.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-08_POINT TYPE_HCD-08 | HCD-08 | POINT TYPE | HCD-08 | GDS.HCD-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-08.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-09_POINT TYPE_HCD-09 | HCD-09 | POINT TYPE | HCD-09 | GDS.HCD-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-09.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-10_POINT TYPE_HCD-10 | HCD-10 | POINT TYPE | HCD-10 | GDS.HCD-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-10.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-11_POINT TYPE_HCD-11 | HCD-11 | POINT TYPE | HCD-11 | GDS.HCD-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-11.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-11.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-12_POINT TYPE_HCD-12 | HCD-12 | POINT TYPE | HCD-12 | GDS.HCD-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-12.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-12.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-13_POINT TYPE_HCD-13 | HCD-13 | POINT TYPE | HCD-13 | GDS.HCD-13.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-13.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-13.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-13.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-13.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-14_POINT TYPE_HCD-14 | HCD-14 | POINT TYPE | HCD-14 | GDS.HCD-14.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-14.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-14.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-14.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-14.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-15_POINT TYPE_HCD-15 | HCD-15 | POINT TYPE | HCD-15 | GDS.HCD-15.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-15.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-15.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-15.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-15.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-16_POINT TYPE_HCD-16 | HCD-16 | POINT TYPE | HCD-16 | GDS.HCD-16.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-16.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-16.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-16.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-16.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | HCD-17_POINT TYPE_HCD-17 | HCD-17 | POINT TYPE | HCD-17 | GDS.HCD-17.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-17.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-17.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-17.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-17.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1221 | Delhi | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | DV-06 | DRAINVALVE.DV-06.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | DV-07 | DRAINVALVE.DV-07.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | DV-08 | DRAINVALVE.DV-08.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | DV-09 | DRAINVALVE.DV-09.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | Normal value | BARRIER GATE LR STATUS | Normal value
1221 | Delhi | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1221 | Delhi | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | Normal Value
1221 | Delhi | Hooter1_EFFECT_HOOTER_FOR_DYKE_FWP_CR | Hooter1 | EFFECT_HOOTER_FOR_DYKE_FWP_CR | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1221 | Delhi | Hooter2_EFFECT_HOOTER_FOR_ESD_CR | Hooter2 | EFFECT_HOOTER_FOR_ESD_CR | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1221 | Delhi | Hooter3_EFFECT_HOOTER_FOR_HC_CR | Hooter3 | EFFECT_HOOTER_FOR_HC_CR | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1221 | Delhi | Hooter4_EFFECT_HOOTER_FOR_HC_FIELD | Hooter4 | EFFECT_HOOTER_FOR_HC_FIELD | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_FIELD | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | Normal Value | ESD MAINTENANCE STATUS | Normal Value | All ROSOVs closed | Normal Value | Barrier Gate opened | Normal Value | TLF Gantry Permissive Power Off | Normal Value | All TLF Product Pumps Stopped | Normal Value | All Tanks in Dormant Mode | Normal Value | All DBBVs Closed | Normal Value | ESD Command To Process PLC | Normal Value | Siren Activated | Normal Value | ESD Hooter activated in control room | Normal Value | Power ESD Activation after 120 Sec | Normal Value | TTL Dispatch in Dormant Mode | Normal Value
1221 | Delhi | ESD-01_SECURITY ROOM | ESD-01 | ESD-01 | SECURITY ROOM | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-02_TERMINAL MANAGER ROOM | ESD-02 | ESD-02 | TERMINAL MANAGER ROOM | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-03_LICENSE ENTRY GATE | ESD-03 | ESD-03 | LICENSE ENTRY GATE | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-04_BAY-04 GANTRY 01 | ESD-04 | ESD-04 | BAY-04 GANTRY 01 | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-05_BAY-09 GANTRY 02 | ESD-05 | ESD-05 | BAY-09 GANTRY 02 | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-06_BAY-18 GANTRY 03 | ESD-06 | ESD-06 | BAY-18 GANTRY 03 | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-07_BAY-12 GANTRY 02 | ESD-07 | ESD-07 | BAY-12 GANTRY 02 | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-08_SAMPLE ROOM | ESD-08 | ESD-08 | SAMPLE ROOM | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-09_PUMP HOUSE | ESD-09 | ESD-09 | PUMP HOUSE | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-10_MCC ROOM | ESD-10 | ESD-10 | MCC ROOM | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-11_NEAR TANK 08 | ESD-11 | ESD-11 | NEAR TANK 08 | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-12_NEAR TANK 03 | ESD-12 | ESD-12 | NEAR TANK 03 | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-13_ETP | ESD-13 | ESD-13 | ETP | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-14_CONTROL ROOM | ESD-14 | ESD-14 | CONTROL ROOM | ESD.ESD-14.ESD_STATUS | 0 | ESD.ESD-14.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-CENTRAL_ESD-CENTRAL | ESD-CENTRAL | ESD-CENTRAL | ESD-CENTRAL | ESD.ESD-CENTRAL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-POWER_ESD-POWER | ESD-POWER | ESD-POWER | ESD-POWER | ESD.ESD-POWER.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-PPL_ESD-PPL | ESD-PPL | ESD-PPL | ESD-PPL | ESD.ESD-PPL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-RIO_ESD-RIO | ESD-RIO | ESD-RIO | ESD-RIO | ESD.ESD-RIO.ESD_STATUS | 0 | ESD.ESD-RIO.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0
1221 | Delhi | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 | ESD.ESD-SOFT.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_COMMAND_TO_PROCESS_PLC | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1221 | Delhi | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 02_BC-01B_BS VI MS | LP 02 | TLF | BC-01B | BS VI MS | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 03_BC-02A_BS VI MS | LP 03 | TLF | BC-02A | BS VI MS | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 04_BC-02B_BS VI MS | LP 04 | TLF | BC-02B | BS VI MS | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 05_BC-03A_BS VI MS | LP 05 | TLF | BC-03A | BS VI MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 06_BC-03B_BS VI MS | LP 06 | TLF | BC-03B | BS VI MS | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 07_BC-04A_BS VI MS | LP 07 | TLF | BC-04A | BS VI MS | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 08_BC-04B_BS VI MS | LP 08 | TLF | BC-04B | BS VI MS | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 09_BC-05A_BS VI MS | LP 09 | TLF | BC-05A | BS VI MS | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 10_BC-05B_BS VI MS | LP 10 | TLF | BC-05B | BS VI MS | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 11_BC-06A_BS VI MS | LP 11 | TLF | BC-06A | BS VI MS | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 13_BC-07A_BS VI MS | LP 13 | TLF | BC-07A | BS VI MS | SmartLoad-Dual.BC-07A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 14_BC-07B_BS VI HSD | LP 14 | TLF | BC-07B | BS VI HSD | SmartLoad-Dual.BC-07B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 15_BC-08A_BS VI MS | LP 15 | TLF | BC-08A | BS VI MS | SmartLoad-Dual.BC-08A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-08A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 16_BC-08B_BS VI HSD | LP 16 | TLF | BC-08B | BS VI HSD | SmartLoad-Dual.BC-08B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-08B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 17_BC-09A_BS VI MS | LP 17 | TLF | BC-09A | BS VI MS | SmartLoad-Dual.BC-09A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 18_BC-09B_BS VI HSD | LP 18 | TLF | BC-09B | BS VI HSD | SmartLoad-Dual.BC-09B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 19_BC-10A_BS VI MS | LP 19 | TLF | BC-10A | BS VI MS | SmartLoad-Dual.BC-10A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 20_BC-10B_BS VI HSD | LP 20 | TLF | BC-10B | BS VI HSD | SmartLoad-Dual.BC-10B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 21_BC-11A_BS VI MS | LP 21 | TLF | BC-11A | BS VI MS | SmartLoad-Dual.BC-11A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-11A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 22_BC-11B_BS VI HSD | LP 22 | TLF | BC-11B | BS VI HSD | SmartLoad-Dual.BC-11B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-11B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-11B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-11B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-11B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 23_BC-12A_BS VI MS | LP 23 | TLF | BC-12A | BS VI MS | SmartLoad-Dual.BC-12A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-12A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 24_BC-12B_BS VI HSD | LP 24 | TLF | BC-12B | BS VI HSD | SmartLoad-Dual.BC-12B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-12B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-12B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-12B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-12B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 25_BC-13A_BS VI HSD | LP 25 | TLF | BC-13A | BS VI HSD | SmartLoad-Dual.BC-13A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 26_BC-13B_BS VI HSD | LP 26 | TLF | BC-13B | BS VI HSD | SmartLoad-Dual.BC-13B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 27_BC-14A_BS VI HSD | LP 27 | TLF | BC-14A | BS VI HSD | SmartLoad-Dual.BC-14A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-14A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-14A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 28_BC-14B_BS VI HSD | LP 28 | TLF | BC-14B | BS VI HSD | SmartLoad-Dual.BC-14B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-14B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 29_BC-15A_BS VI HSD | LP 29 | TLF | BC-15A | BS VI HSD | SmartLoad-Dual.BC-15A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-15A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-15A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 30_BC-15B_BS VI HSD | LP 30 | TLF | BC-15B | BS VI HSD | SmartLoad-Dual.BC-15B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-15B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 31_BC-16A_BS VI HSD | LP 31 | TLF | BC-16A | BS VI HSD | SmartLoad-Dual.BC-16A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-16A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 32_BC-16B_BS VI HSD | LP 32 | TLF | BC-16B | BS VI HSD | SmartLoad-Dual.BC-16B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-16B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 33_BC-17A_BS VI HSD | LP 33 | TLF | BC-17A | BS VI HSD | SmartLoad-Dual.BC-17A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-17A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-17A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-17A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-17A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-17A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-17A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 34_BC-17B_SOLVENT | LP 34 | TLF | BC-17B | SOLVENT | SmartLoad-Dual.BC-17B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-17B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-17B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-17B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-17B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-17B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 35_BC-18A_BS VI HSD | LP 35 | TLF | BC-18A | BS VI HSD | SmartLoad-Dual.BC-18A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-18A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-18A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-18A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-18A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-18A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-18A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 36_BC-18B_SOLVENT | LP 36 | TLF | BC-18B | SOLVENT | SmartLoad-Dual.BC-18B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-18B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-18B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-18B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-18B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-18B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 37_BC-19A_BS VI HSD | LP 37 | TLF | BC-19A | BS VI HSD | SmartLoad-Dual.BC-19A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-19A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-19A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-19A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-19A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-19A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-19A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 38_BC-19B_BS VI HSD | LP 38 | TLF | BC-19B | BS VI HSD | SmartLoad-Dual.BC-19B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-19B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-19B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-19B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-19B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-19B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 39_BC-20A_BS VI HSD | LP 39 | TLF | BC-20A | BS VI HSD | SmartLoad-Dual.BC-20A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-20A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-20A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-20A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-20A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-20A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-20A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1221 | Delhi | LP 40_BC-20B_BS VI HSD | LP 40 | TLF | BC-20B | BS VI HSD | SmartLoad-Dual.BC-20B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-20B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-20B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-20B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-20B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-20B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1221 | Delhi | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1221 | Delhi | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1221 | Delhi | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1221 | Delhi | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1221 | Delhi | WATER Level below Ref. Volume | PLC.SFTPLC.CAUSE_WATERTK_VOL_BELOW_90PCT | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1221 | Delhi | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_FEP_IN_LOCAL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1221 | Delhi | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1221 | Delhi | LRC Switch Over | CLIENT.LRC1.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Fire Engine4 | Normal Value | Fire Engine5 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1221 | Delhi | Operability Index | PUMP.FWP-01.ON | 0 | PUMP.FWP-02.ON | 0 | PUMP.FWP-03.ON | 0 | PUMP.FWP-04.ON | 0 | PUMP.FWP-05.ON | 0 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.FPT-01.PRESSURE |  | PressureTransmitter.FPT-02.PRESSURE |  | PLC.SFTPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_FEP_IN_LOCAL | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1