## Tank Master
` | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1259 | Srinagar | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-01.OPEN_STATUS | 0 | DBBV-01 | MOV IL1 |  |  |  |  | MOV.DBBV-02.OPEN_STATUS | 0 | DBBV-02 | MOV OL
1259 | Srinagar | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-03.OPEN_STATUS | 0 | DBBV-03 | MOV IL1 |  |  |  |  | MOV.DBBV-04.OPEN_STATUS | 0 | DBBV-04 | MOV OL
1259 | Srinagar | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-05.OPEN_STATUS | 0 | DBBV-05 | MOV IL1 |  |  |  |  | MOV.DBBV-06.OPEN_STATUS | 0 | DBBV-06 | MOV OL
1259 | Srinagar | TK-04_BS VI HSD | TK-04 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-07.OPEN_STATUS | 0 | DBBV-07 | MOV IL1 |  |  |  |  | MOV.DBBV-08.OPEN_STATUS | 0 | DBBV-08 | MOV OL
1259 | Srinagar | TK-05_BS VI HSD | TK-05 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-09.OPEN_STATUS | 0 | DBBV-09 | MOV IL1 |  |  |  |  | MOV.DBBV-10.OPEN_STATUS | 0 | DBBV-10 | MOV OL
1259 | Srinagar | TK-06_BS VI HSD | TK-06 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-11.OPEN_STATUS | 0 | DBBV-11 | MOV IL1 |  |  |  |  | MOV.DBBV-12.OPEN_STATUS | 0 | DBBV-12 | MOV OL
1259 | Srinagar | TK-07_BS VI HSD | TK-07 | UG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar
1259 | Srinagar | TK-08_NAPHTHA | TK-08 | UG | NAPHTHA | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1259 | Srinagar | TK-09_NAPHTHA | TK-09 | UG | NAPHTHA | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1259 | Srinagar | TK-10_NAPHTHA | TK-10 | UG | NAPHTHA | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1259 | Srinagar | WTK-01_BS VI MS | WTK-01 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.WTK-01.LEVEL |  | WTK-01 | Primary Radar
1259 | Srinagar | WTK-02_BS VI MS | WTK-02 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.WTK-02.LEVEL |  | WTK-02 | Primary Radar
1259 | Srinagar | WTK-03_BS VI MS | WTK-03 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.WTK-03.LEVEL |  | WTK-03 | Primary Radar

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1259 | Srinagar_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL |  |  |  |  | MOV.DBBV-01.MAINTENANCE_STATUS | 0 | DBBV-01 | RADAR | [8 empty] | MOV.DBBV-02.MAINTENANCE_STATUS | 0 | DBBV-02 | MOV OL
1259 | Srinagar_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV OL |  |  |  |  | MOV.DBBV-03.MAINTENANCE_STATUS | 0 | DBBV-03 | RADAR | [8 empty] | MOV.DBBV-04.MAINTENANCE_STATUS | 0 | DBBV-04 | MOV OL
1259 | Srinagar_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV OL |  |  |  |  | MOV.DBBV-05.MAINTENANCE_STATUS | 0 | DBBV-05 | RADAR | [8 empty] | MOV.DBBV-06.MAINTENANCE_STATUS | 0 | DBBV-06 | MOV OL
1259 | Srinagar_M | TK-04_BS VI HSD | TK-04 | AG | BS VI HSD | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL |  |  |  |  | MOV.DBBV-07.MAINTENANCE_STATUS | 0 | DBBV-07 | RADAR | [8 empty] | MOV.DBBV-08.MAINTENANCE_STATUS | 0 | DBBV-08 | MOV OL
1259 | Srinagar_M | TK-05_BS VI HSD | TK-05 | AG | BS VI HSD | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV OL |  |  |  |  | MOV.DBBV-09.MAINTENANCE_STATUS | 0 | DBBV-09 | RADAR | [8 empty] | MOV.DBBV-10.MAINTENANCE_STATUS | 0 | DBBV-10 | MOV OL
1259 | Srinagar_M | TK-06_BS VI HSD | TK-06 | AG | BS VI HSD | TANK.TK-06.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV OL |  |  |  |  | MOV.DBBV-11.MAINTENANCE_STATUS | 0 | DBBV-11 | RADAR | [8 empty] | MOV.DBBV-12.MAINTENANCE_STATUS | 0 | DBBV-12 | MOV OL
1259 | Srinagar_M | TK-07_BS VI HSD | TK-07 | UG | BS VI HSD | TANK.TK-07.MAINTENANCE_STATUS | 0
1259 | Srinagar_M | TK-08_NAPHTHA | TK-08 | UG | NAPHTHA | TANK.TK-08.MAINTENANCE_STATUS | 0
1259 | Srinagar_M | TK-09_NAPHTHA | TK-09 | UG | NAPHTHA | TANK.TK-09.MAINTENANCE_STATUS | 0
1259 | Srinagar_M | TK-10_NAPHTHA | TK-10 | UG | NAPHTHA | TANK.TK-10.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1259 | Srinagar | ADTV-PMP-01_POWERMS_DISPATCH | ADTV-PMP-01 | POWERMS | TLF | DISPATCH | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.OFF | 1 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1259 | Srinagar | ADTV-PMP-02_POWERMS_DISPATCH | ADTV-PMP-02 | POWERMS | TLF | DISPATCH | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.OFF | 1 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1259 | Srinagar | ADTV-PMP-03_TURBOHSD_DISPATCH | ADTV-PMP-03 | TURBOHSD | TLF | DISPATCH | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.OFF | 1 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1259 | Srinagar | ADTV-PMP-04_TURBOHSD_DISPATCH | ADTV-PMP-04 | TURBOHSD | TLF | DISPATCH | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.OFF | 1 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-01_ETHANOL_DISPATCH | PMP-01 | ETHANOL | TLF | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.OFF | 1 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-02_BS VI GASOHOL_DISPATCH | PMP-02 | BS VI GASOHOL | TLF | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.OFF | 1 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-03_BS VI GASOHOL_DISPATCH | PMP-03 | BS VI GASOHOL | TLF | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.OFF | 1 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.OFF | 1 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-05_BS VI HSD_DISPATCH | PMP-05 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.OFF | 1 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-06_SKO_DISPATCH | PMP-06 | SKO | TLF | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.OFF | 1 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-07_SKO_DISPATCH | PMP-07 | SKO | TLF | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.OFF | 1 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-08_ATF_DISPATCH | PMP-08 | ATF | TLF | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.OFF | 1 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-09_ATF_DISPATCH | PMP-09 | ATF | TLF | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.OFF | 1 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-10_ATF_DISPATCH | PMP-10 | ATF | TLF | DISPATCH | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.OFF | 1 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-11_ATF_DISPATCH | PMP-11 | ATF | TLF | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.OFF | 1 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-12_BS VI MS_DISPATCH | PMP-12 | BS VI MS | TLF | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.OFF | 1 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1259 | Srinagar | PMP-13_BS VI MS_DISPATCH | PMP-13 | BS VI MS | TLF | DISPATCH | PUMP.PMP-13.ON | 0 | PUMP.PMP-13.OFF | 1 | PUMP.PMP-13.REMOTE_STATUS | 1 | PUMP.PMP-13.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1259 | Srinagar | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.OFF | 1 | PUMP.FWP-01.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.OFF | 1 | PUMP.FWP-02.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.OFF | 1 | PUMP.FWP-03.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | FWP-04_Water_DISPATCH | FWP-04 | Water | PH | DISPATCH | PUMP.FWP-04.ON | 0 | PUMP.FWP-04.OFF | 1 | PUMP.FWP-04.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-04.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | FWP-05_Water_DISPATCH | FWP-05 | Water | PH | DISPATCH | PUMP.FWP-05.ON | 0 | PUMP.FWP-05.OFF | 1 | PUMP.FWP-05.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-05.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | FWP-06_Water_DISPATCH | FWP-06 | Water | PH | DISPATCH | PUMP.FWP-06.ON | 0 | PUMP.FWP-06.OFF | 1 | PUMP.FWP-06.REMOTE_STATUS | 1 | [14 empty] | PUMP.FWP-06.HIGH_TEMPERATURE_ALARM | 0
1259 | Srinagar | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.OFF | 1 | PUMP.JCY-01.REMOTE_STATUS | 1
1259 | Srinagar | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.OFF | 1 | PUMP.JCY-02.REMOTE_STATUS | 1
1259 | Srinagar | Farthest Point PT_WATER Pressure_Near Tank no. 01 | Farthest Point PT | WATER Pressure | PT | Near Tank no. 01 | [6 empty] | PressureTransmitter.FPT-01.MAINTENANCE_STATUS | 0
1259 | Srinagar | Nearest Point PT_WATER Pressure_FWP pump house | Nearest Point PT | WATER Pressure | PT | FWP pump house | [6 empty] | PressureTransmitter.FPT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1259 | Srinagar | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 |  |  | UPS.UPS-01.MAIN_AC_FAIL | 0
1259 | Srinagar | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 |  |  | UPS.UPS-02.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1259 | Srinagar | GEPLC_Process PLC | GEPLC | Process PLC | PLC.GEPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.GEPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1259 | Srinagar | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1128 | Mathura | HDS-01_OPEN TYPE_NEW TWD PUMP HOUSE | HDS-01 | OPEN TYPE | NEW TWD PUMP HOUSE | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-02_OPEN TYPE_OLD TWD PUMP HOUSE | HDS-02 | OPEN TYPE | OLD TWD PUMP HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-03_OPEN TYPE_NEAR TANK - 01 | HDS-03 | OPEN TYPE | NEAR TANK - 01 | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0
1259 | Srinagar | HCD-01_POINT_TYPE_NEAR TK-02 DYKE | HCD-01 | POINT_TYPE | NEAR TK-02 DYKE | GDS.HCD-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-01.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1128 | Mathura | HDS-05_OPEN TYPE_NEAR TANK - 24 | HDS-05 | OPEN TYPE | NEAR TANK - 24 | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-06_OPEN TYPE_NEAR TANK -25 | HDS-06 | OPEN TYPE | NEAR TANK -25 | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-06.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-07_OPEN TYPE_TLF PUMP HOUSE | HDS-07 | OPEN TYPE | TLF PUMP HOUSE | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-09_OPEN PATH_NEAR TANK - 20 | HDS-09 | OPEN PATH | NEAR TANK - 20 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-11_OPEN PATH_NEAR UG PUMP HOUSE | HDS-11 | OPEN PATH | NEAR UG PUMP HOUSE | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-11.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-11.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-12_OPEN PATH_NEAR TK-5 | HDS-12 | OPEN PATH | NEAR TK-5 | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-12.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-12.MAINTENANCE_CALL | 0
1259 | Srinagar | HCD-02_OPEN_TYPE_TLF PUMP HOUSE | HCD-02 | OPEN_TYPE | TLF PUMP HOUSE | GDS.HCD-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-02.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1259 | Srinagar | HCD-03_OPEN_TYPE_NEAR TK-05 AND TK-06 | HCD-03 | OPEN_TYPE | NEAR TK-05 AND TK-06 | GDS.HCD-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-03.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1259 | Srinagar | HCD-04_POINT_TYPE_GANTRY HEADER LINE | HCD-04 | POINT_TYPE | GANTRY HEADER LINE | GDS.HCD-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-04.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1259 | Srinagar | HCD-05_NEAR_VRU SYSTEM | HCD-05 | NEAR | VRU SYSTEM | GDS.HCD-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HCD-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HCD-05.CRITICAL_FAULT_ALARM | 0 | GDS.HCD-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HCD-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1259 | Srinagar | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1259 | Srinagar | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.CLOSE_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1259 | Srinagar | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.CLOSE_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1259 | Srinagar | Hooter1_ANY_HOOTER_FOR_HCD_FIELD | Hooter1 | ANY_HOOTER_FOR_HCD_FIELD | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1259 | Srinagar | Hooter2_HOOTER_ACK_STATUS | Hooter2 | HOOTER_ACK_STATUS | PLC.SFTPLC.HOOTER_ACK_STATUS | 0
1259 | Srinagar | Hooter3_HOOTER_FOR_ESD_CR | Hooter3 | HOOTER_FOR_ESD_CR | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1259 | Srinagar | Hooter4_HOOTER_FOR_HC_CR | Hooter4 | HOOTER_FOR_HC_CR | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1259 | Srinagar | Hooter5_HOOTER_FOR_RIMSEAL_CR | Hooter5 | HOOTER_FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1259 | Srinagar | Hooter6_HOOTER_RESET_STATUS | Hooter6 | HOOTER_RESET_STATUS | PLC.SFTPLC.HOOTER_RESET_STATUS | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1259 | Srinagar | ESD-01_TM ROOM | ESD-01 | ESD_PB_301 | TM ROOM | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-02_NEAR BARRIER GATE | ESD-02 | ESD_PB_201 | NEAR BARRIER GATE | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-03_GANTRY BAY 1 DOWN SIDE | ESD-03 | ESD_PB_501 | GANTRY BAY 1 DOWN SIDE | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-04_MCC FRONT SIDE | ESD-04 | ESD_PB_601 | MCC FRONT SIDE | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-05_NEAR TANK 05 | ESD-05 | ESD_PB_901 | NEAR TANK 05 | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-06_TLF PUMP HOUSE | ESD-06 | ESD_PB_701 | TLF PUMP HOUSE | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-07_ADMIN BUILDING | ESD-07 | ESD_PB_302 | ADMIN BUILDING | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-08_GANTRY CATWAY BAY 04 | ESD-08 | ESD_PB_502 | GANTRY CATWAY BAY 04 | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-09_NEAR TANK 02 | ESD-09 | ESD_PB_902 | NEAR TANK 02 | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-10_CENTRAL ESD | ESD-10 | ESD-CENTRAL | CENTRAL ESD | ESD.ESD-10.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1259 | Srinagar | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1259 | Srinagar | LP 01_BC-01A_BS VI HSD | LP 01 | TLF | BC-01A | BS VI HSD | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 02_BC-01B_BS VI GASOHOL | LP 02 | TLF | BC-01B | BS VI GASOHOL | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 03_BC-02A_BS VI HSD | LP 03 | TLF | BC-02A | BS VI HSD | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 04_BC-02B_BS VI GASOHOL | LP 04 | TLF | BC-02B | BS VI GASOHOL | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 05_BC-03A_BS VI HSD | LP 05 | TLF | BC-03A | BS VI HSD | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 06_BC-03B_BS VI GASOHOL | LP 06 | TLF | BC-03B | BS VI GASOHOL | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 07_BC-04A_BS VI HSD | LP 07 | TLF | BC-04A | BS VI HSD | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 08_BC-04B_BS VI GASOHOL | LP 08 | TLF | BC-04B | BS VI GASOHOL | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 09_BC-05A_BS VI HSD | LP 09 | TLF | BC-05A | BS VI HSD | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 10_BC-05B_SKO | LP 10 | TLF | BC-05B | SKO | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 11_BC-06A_BS VI HSD | LP 11 | TLF | BC-06A | BS VI HSD | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1259 | Srinagar | LP 12_BC-06B_ATF | LP 12 | TLF | BC-06B | ATF | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1259 | Srinagar | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1259 | Srinagar | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1259 | Srinagar | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1259 | Srinagar | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1259 | Srinagar | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1259 | Srinagar | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1259 | Srinagar | Gantry Permissive Off |  |  | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1259 | Srinagar | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Fire Engine4 | Normal Value | Fire Engine5 | Normal Value | Fire Engine6 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1259 | Srinagar | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-04.REMOTE_STATUS | 1 | PUMP.FWP-05.REMOTE_STATUS | 1 | PUMP.FWP-06.REMOTE_STATUS | 1 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.FPT-02.PRESSURE |  | PressureTransmitter.FPT-01.PRESSURE |  | PLC.GEPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 |  |  | PUMP.JCY-02.REMOTE_STATUS