## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1424 | Jabalpur | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED RCL | MOV.MOV-001.OPEN_STATUS | 0 | MOV-001 | MOV IL1 |  |  |  |  | MOV.MOV-002.OPEN_STATUS | 0 | MOV-002 | MOV OL | MOV.MOV-003.OPEN_STATUS | 0 | MOV-003 | MOV RCL
1424 | Jabalpur | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV IL1 | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED OL | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED RCL | MOV.MOV-004.OPEN_STATUS | 0 | MOV-004 | MOV IL1 |  |  |  |  | MOV.MOV-005.OPEN_STATUS | 0 | MOV-005 | MOV OL | MOV.MOV-006.OPEN_STATUS | 0 | MOV-006 | MOV RCL
1424 | Jabalpur | TK-03_BS VI MS | TK-03 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED RCL | MOV.MOV-007.OPEN_STATUS | 0 | MOV-007 | MOV IL1 |  |  |  |  | MOV.MOV-008.OPEN_STATUS | 0 | MOV-008 | MOV OL | MOV.MOV-009.OPEN_STATUS | 0 | MOV-009 | MOV RCL
1424 | Jabalpur | TK-04_BS VI MS | TK-04 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV IL1 | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED OL | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED RCL | MOV.MOV-010.OPEN_STATUS | 0 | MOV-010 | MOV IL1 |  |  |  |  | MOV.MOV-011.OPEN_STATUS | 0 | MOV-011 | MOV OL | MOV.MOV-012.OPEN_STATUS | 0 | MOV-012 | MOV RCL
1424 | Jabalpur | TK-05_ETHANOL | TK-05 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED RCL | MOV.MOV-013.OPEN_STATUS | 0 | MOV-013 | MOV IL1 |  |  |  |  | MOV.MOV-014.OPEN_STATUS | 0 | MOV-014 | MOV OL | MOV.MOV-015.OPEN_STATUS | 0 | MOV-015 | MOV RCL
1424 | Jabalpur | TK-06_WATER | TK-06 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | [12 empty] | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR
1424 | Jabalpur | TK-07_WATER | TK-07 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar | [12 empty] | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR
1424 | Jabalpur | TK-08_FO | TK-08 | AG | FO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1424 | Jabalpur | TK-09_FO | TK-09 | AG | FO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1424 | Jabalpur | TK-10_BS VI MS | TK-10 | UG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1424 | Jabalpur | TK-11_ETHANOL | TK-11 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar |  |  | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.TANK_ALERT_ALARM | 0 | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar
1424 | Jabalpur | TK-12_BS VI HSD | TK-12 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM | 0 | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar
1424 | Jabalpur | TK-13_ETHANOL | TK-13 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.TANK_ALERT_ALARM | 0 | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar
1424 | Jabalpur | TK-14_ETHANOL | TK-14 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar
1424 | Jabalpur | TK-15_ETHANOL | TK-15 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1424 | Jabalpur_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.MOV-001.MAINTENANCE_STATUS | 0 | MOV-001 | MOV IL1 |  |  |  |  | MOV.MOV-003.MAINTENANCE_STATUS | 0 | MOV-003 | MOV RCL | MOV.MOV-002.MAINTENANCE_STATUS | 0 | MOV-002 | MOV OL
1424 | Jabalpur_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV RCL | MOV.MOV-004.MAINTENANCE_STATUS | 0 | MOV-004 | MOV IL1 |  |  |  |  | MOV.MOV-006.MAINTENANCE_STATUS | 0 | MOV-006 | MOV RCL | MOV.MOV-005.MAINTENANCE_STATUS | 0 | MOV-005 | MOV OL
1424 | Jabalpur_M | TK-03_BS VI MS | TK-03 | AG | BS VI MS | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.MOV-007.MAINTENANCE_STATUS | 0 | MOV-007 | MOV IL1 |  |  |  |  | MOV.MOV-009.MAINTENANCE_STATUS | 0 | MOV-009 | MOV RCL | MOV.MOV-008.MAINTENANCE_STATUS | 0 | MOV-008 | MOV OL
1424 | Jabalpur_M | TK-04_BS VI MS | TK-04 | AG | BS VI MS | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV RCL | MOV.MOV-010.MAINTENANCE_STATUS | 0 | MOV-010 | MOV IL1 |  |  |  |  | MOV.MOV-012.MAINTENANCE_STATUS | 0 | MOV-012 | MOV RCL | MOV.MOV-011.MAINTENANCE_STATUS | 0 | MOV-011 | MOV OL
1424 | Jabalpur_M | TK-05_ETHANOL | TK-05 | AG | ETHANOL | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.MOV-013.MAINTENANCE_STATUS | 0 | MOV-013 | MOV IL1 |  |  |  |  | MOV.MOV-015.MAINTENANCE_STATUS | 0 | MOV-015 | MOV RCL | MOV.MOV-014.MAINTENANCE_STATUS | 0 | MOV-014 | MOV OL
1424 | Jabalpur_M | TK-06_WATER | TK-06 | AG | WATER | TANK.TK-06.MAINTENANCE_STATUS | 0
1424 | Jabalpur_M | TK-07_WATER | TK-07 | AG | WATER | TANK.TK-07.MAINTENANCE_STATUS | 0
1424 | Jabalpur_M | TK-08_FO | TK-08 | AG | FO | TANK.TK-08.MAINTENANCE_STATUS | 0
1424 | Jabalpur_M | TK-09_FO | TK-09 | AG | FO | TANK.TK-09.MAINTENANCE_STATUS | 0
1424 | Jabalpur_M | TK-15_ETHANOL | TK-15 | UG | ETHANOL | TANK.TK-15.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1424 | Jabalpur | ADTV-PMP-01_POWERMS_DISPATCH | ADTV-PMP-01 | POWERMS | TLF | DISPATCH | PUMP.ADTV-PMP-01.ON | FLASE | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1424 | Jabalpur | ADTV-PMP-02_POWERMS_DISPATCH | ADTV-PMP-02 | POWERMS | TLF | DISPATCH | PUMP.ADTV-PMP-02.ON | FLASE | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1424 | Jabalpur | ADTV-PMP-03_TURBOHSD_DISPATCH | ADTV-PMP-03 | TURBOHSD | TLF | DISPATCH | PUMP.ADTV-PMP-03.ON | FLASE | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1424 | Jabalpur | ADTV-PMP-04_TURBOHSD_DISPATCH | ADTV-PMP-04 | TURBOHSD | TLF | DISPATCH | PUMP.ADTV-PMP-04.ON | FLASE | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1424 | Jabalpur | ADTV-PMP-05_BLUE DYE_DISPATCH | ADTV-PMP-05 | BLUE DYE | TLF | DISPATCH | PUMP.ADTV-PMP-05.ON | FLASE | PUMP.ADTV-PMP-05.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-05.MAINTENANCE_STATUS | 0
1424 | Jabalpur | ADTV-PMP-06_BLUE DYE_DISPATCH | ADTV-PMP-06 | BLUE DYE | TLF | DISPATCH | PUMP.ADTV-PMP-06.ON | FLASE | PUMP.ADTV-PMP-06.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-06.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-01_BS VI MS_DISPATCH | PMP-01 | BS VI MS | TLF | DISPATCH | PUMP.PMP-01.ON | FLASE | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-02_BS VI MS_DISPATCH | PMP-02 | BS VI MS | TLF | DISPATCH | PUMP.PMP-02.ON | FLASE | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-03_BS VI MS_DISPATCH | PMP-03 | BS VI MS | TLF | DISPATCH | PUMP.PMP-03.ON | FLASE | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-04_BS VI MS_DISPATCH | PMP-04 | BS VI MS | TLF | DISPATCH | PUMP.PMP-04.ON | FLASE | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-05_BS VI HSD_DISPATCH | PMP-05 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-05.ON | FLASE | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-06_BS VI HSD_DISPATCH | PMP-06 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-06.ON | FLASE | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-07_BS VI HSD_DISPATCH | PMP-07 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-07.ON | FLASE | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-08_BS VI HSD_DISPATCH | PMP-08 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-08.ON | FLASE | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-09_BS VI HSD_DISPATCH | PMP-09 | BS VI HSD | TLF | DISPATCH | PUMP.PMP-09.ON | FLASE | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-11_ETHANOL_DISPATCH | PMP-11 | ETHANOL | TLF | DISPATCH | PUMP.PMP-11.ON | FLASE | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-12_ETHANOL_DISPATCH | PMP-12 | ETHANOL | TLF | DISPATCH | PUMP.PMP-12.ON | FLASE | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-14_FO_DISPATCH | PMP-14 | FO | TLF | DISPATCH | PUMP.PMP-14.ON | FLASE | PUMP.PMP-14.REMOTE_STATUS | 1 | PUMP.PMP-14.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-15_FO_DISPATCH | PMP-15 | FO | TLF | DISPATCH | PUMP.PMP-15.ON | FLASE | PUMP.PMP-15.REMOTE_STATUS | 1 | PUMP.PMP-15.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-16_ETHANOL_DISPATCH | PMP-16 | ETHANOL | TLF | DISPATCH | PUMP.PMP-16.ON | FLASE | PUMP.PMP-16.REMOTE_STATUS | 1 | PUMP.PMP-16.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-17_ETHANOL_DISPATCH | PMP-17 | ETHANOL | TLF | DISPATCH | PUMP.PMP-17.ON | FLASE | PUMP.PMP-17.REMOTE_STATUS | 1 | PUMP.PMP-17.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-18_FO_RECEIPT | PMP-18 | FO | WL | RECEIPT | PUMP.PMP-18.ON | FLASE | PUMP.PMP-18.REMOTE_STATUS | 1 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-19_FO_RECEIPT | PMP-19 | FO | WL | RECEIPT | PUMP.PMP-19.ON | FLASE | PUMP.PMP-19.REMOTE_STATUS | 1 | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-20_FO_RECEIPT | PMP-20 | FO | WL | RECEIPT | PUMP.PMP-20.ON | FLASE | PUMP.PMP-20.REMOTE_STATUS | 1 | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-21_BS VI HSD_RECEIPT | PMP-21 | BS VI HSD | WL | RECEIPT | PUMP.PMP-21.ON | FLASE | PUMP.PMP-21.REMOTE_STATUS | 1 | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-22_BS VI HSD_RECEIPT | PMP-22 | BS VI HSD | WL | RECEIPT | PUMP.PMP-22.ON | FLASE | PUMP.PMP-22.REMOTE_STATUS | 1 | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-23_ETHANOL_RECEIPT | PMP-23 | ETHANOL | WL | RECEIPT | PUMP.PMP-23.ON | FLASE | PUMP.PMP-23.REMOTE_STATUS | 1 | PUMP.PMP-23.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-24_ETHANOL_RECEIPT | PMP-24 | ETHANOL | WL | RECEIPT | PUMP.PMP-24.ON | FLASE | PUMP.PMP-24.REMOTE_STATUS | 1 | PUMP.PMP-24.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-25_BS VI MS_RECEIPT | PMP-25 | BS VI MS | WL | RECEIPT | PUMP.PMP-25.ON | FLASE | PUMP.PMP-25.REMOTE_STATUS | 1 | PUMP.PMP-25.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-26_BS VI MS_RECEIPT | PMP-26 | BS VI MS | WL | RECEIPT | PUMP.PMP-26.ON | FLASE | PUMP.PMP-26.REMOTE_STATUS | 1 | PUMP.PMP-26.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-27_WATER_DISPATCH | PMP-27 | WATER | TLF | DISPATCH | PUMP.PMP-27.ON | FLASE | PUMP.PMP-27.REMOTE_STATUS | 1 | PUMP.PMP-27.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-28_WATER_DISPATCH | PMP-28 | WATER | TLF | DISPATCH | PUMP.PMP-28.ON | FLASE | PUMP.PMP-28.REMOTE_STATUS | 1 | PUMP.PMP-28.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-29_WATER_DISPATCH | PMP-29 | WATER | TLF | DISPATCH | PUMP.PMP-29.ON | FLASE | PUMP.PMP-29.REMOTE_STATUS | 1 | PUMP.PMP-29.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-30_WATER_DISPATCH | PMP-30 | WATER | TLF | DISPATCH | PUMP.PMP-30.ON | FLASE | PUMP.PMP-30.REMOTE_STATUS | 1 | PUMP.PMP-30.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-31_BS VI HSD_DISPATCH | PMP-31 | BS VI HSD | WL | DISPATCH | PUMP.PMP-31.ON | FLASE | PUMP.PMP-31.REMOTE_STATUS | 1 | PUMP.PMP-31.MAINTENANCE_STATUS | 0
1424 | Jabalpur | PMP-32_BS VI MS_DISPATCH | PMP-32 | BS VI MS | WL | DISPATCH | PUMP.PMP-32.ON | FLASE | PUMP.PMP-32.REMOTE_STATUS | 1 | PUMP.PMP-32.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1424 | Jabalpur | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1424 | Jabalpur | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1424 | Jabalpur | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1424 | Jabalpur | JCY-01_Water_DISPATCH | JCY-01 | Water | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-01.PUMP_TRIPPED | 0
1424 | Jabalpur | JCY-02_Water_DISPATCH | JCY-02 | Water | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-02.PUMP_TRIPPED | 0
1424 | Jabalpur | Farthest Point PT_WP_DISPATCH | Farthest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1424 | Jabalpur | Nearest Point PT_WP_DISPATCH | Nearest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1424 | Jabalpur | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.LOAD_ON_UPS | 0 | UPS.UPS-01.MAIN_AC_FAIL | 0
1424 | Jabalpur | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.LOAD_ON_UPS | 0 | UPS.UPS-02.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1424 | Jabalpur | GEPLC_Process PLC | GEPLC | Process PLC | PLC.GEPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.GEPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1424 | Jabalpur | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1424 | Jabalpur | HDS-01_POINT_TYP_TTL PUMP HOUSE | HDS-01 | POINT_TYP | TTL PUMP HOUSE | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-02_POINT_TYP_TANKFARM TK-22 MS | HDS-02 | POINT_TYP | TANKFARM TK-22 MS | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-03_POINT_TYP_TWD PUMP HOUSE | HDS-03 | POINT_TYP | TWD PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-04_FIXED-TYP_TTL PUMP HOUSE | HDS-04 | FIXED-TYP | TTL PUMP HOUSE | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-05_FIXED-TYP_TANKFARM TK-24 SKO | HDS-05 | FIXED-TYP | TANKFARM TK-24 SKO | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-06_FIXED-TYP_TWD PUMP HOUSE | HDS-06 | FIXED-TYP | TWD PUMP HOUSE | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-07_POINT_TYP_NEAR MANIFOLD TK-22 | HDS-07 | POINT_TYP | NEAR MANIFOLD TK-22 | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-08_POINT_TYP_NEAR MANIFOLD TK-23 | HDS-08 | POINT_TYP | NEAR MANIFOLD TK-23 | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-09_POINT_TYP_NEAR MANIFOLD TK-24 | HDS-09 | POINT_TYP | NEAR MANIFOLD TK-24 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-10_POINT_TYP_NEAR VRU SYSTEM | HDS-10 | POINT_TYP | NEAR VRU SYSTEM | GDS.HDS-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-10.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-11_PTD_TANK 09, 10 & 11 | HDS-11 | PTD | TANK 09, 10 & 11 | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-11.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-11.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-12_PTD_TANK 17 | HDS-12 | PTD | TANK 17 | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-12.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-12.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-13_PTD_TANK 18 | HDS-13 | PTD | TANK 18 | GDS.HDS-13.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-13.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-13.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-13.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-13.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | HDS-14_PTD_TANK 19 | HDS-14 | PTD | TANK 19 | GDS.HDS-14.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-14.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-14.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-14.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-14.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1424 | Jabalpur | DV-01 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1424 | Jabalpur | DV-02 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1424 | Jabalpur | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1424 | Jabalpur | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1424 | Jabalpur | HOOTER_HOOTER_FIELD_1 | HOOTER | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_2 | HOOTER | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_3 | HOOTER | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_4 | HOOTER | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_5 | HOOTER | HOOTER_FIELD_5 | PLC.SFTPLC.HOOTER_FIELD_5 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_6 | HOOTER | HOOTER_FIELD_6 | PLC.SFTPLC.HOOTER_FIELD_6 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_7 | HOOTER | HOOTER_FIELD_7 | PLC.SFTPLC.HOOTER_FIELD_9 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_8 | HOOTER | HOOTER_FIELD_8 | PLC.SFTPLC.HOOTER_FIELD_10 | 0
1424 | Jabalpur | HOOTER_HOOTER_FIELD_9 | HOOTER | HOOTER_FIELD_9 | PLC.SFTPLC.HOOTER_FIELD_11 | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1424 | Jabalpur | ESD-01_Inside Contol room | ESD-01 | ESD 01 | Inside Contol room | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-02_Near Control room | ESD-02 | ESD 02 | Near Control room | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-03_Terminal Manager Room | ESD-03 | ESD 03 | Terminal Manager Room | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-04_Near Admin Building | ESD-04 | ESD 04 | Near Admin Building | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-05_MCC DG Shed | ESD-05 | ESD 11 | MCC DG Shed | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-06_Near Security room | ESD-06 | ESD 05 | Near Security room | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-08_Rly.Siding Near BPC Gate | ESD-08 | ESD 12 | Rly.Siding Near BPC Gate | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-09_UG Tank Farm Area | ESD-09 | ESD 13 | UG Tank Farm Area | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-10_Quality Control Lab | ESD-10 | ESD 07 | Quality Control Lab | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-11_Fire Water Pump House | ESD-11 | ESD 08 | Fire Water Pump House | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-12_Rly.Siding Near IOC Gate | ESD-12 | ESD 06 | Rly.Siding Near IOC Gate | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-14_New Gantry Bay no. 06 | ESD-14 | ESD 14 | New Gantry Bay no. 06 | ESD.ESD-14.ESD_STATUS | 0 | ESD.ESD-14.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-15_New Gantry Bay no. 03 | ESD-15 | ESD 15 | New Gantry Bay no. 03 | ESD.ESD-15.ESD_STATUS | 0 | ESD.ESD-15.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-16_MCC Room | ESD-16 | ESD 10 | MCC Room | ESD.ESD-16.ESD_STATUS | 0 | ESD.ESD-16.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-17_TWD MCC Room | ESD-17 | ESD 21 | TWD MCC Room | ESD.ESD-17.ESD_STATUS | 0 | ESD.ESD-17.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-18_TWD Pump House | ESD-18 | ESD 22 | TWD Pump House | ESD.ESD-18.ESD_STATUS | 0 | ESD.ESD-18.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-19_ETP | ESD-19 | ESD 23 | ETP | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-20_Railway siding Entrance Gate | ESD-20 | ESD 24 | Railway siding Entrance Gate | ESD.ESD-20.ESD_STATUS | 0 | ESD.ESD-20.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-22_Near TKHSD 20 | ESD-22 | ESD 17 | Near TKHSD 20 | ESD.ESD-22.ESD_STATUS | 0 | ESD.ESD-22.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-23_Near Future Tank Dyke | ESD-23 | ESD 20 | Near Future Tank Dyke | ESD.ESD-23.ESD_STATUS | 0 | ESD.ESD-23.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-24_Near TKMS 22 | ESD-24 | ESD 18 | Near TKMS 22 | ESD.ESD-24.ESD_STATUS | 0 | ESD.ESD-24.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-25_Near TKMS 23 | ESD-25 | ESD 19 | Near TKMS 23 | ESD.ESD-25.ESD_STATUS | 0 | ESD.ESD-25.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-26_Near TKFO 13 / 14 | ESD-26 | ESD 09 | Near TKFO 13 / 14 | ESD.ESD-26.ESD_STATUS | 0 | ESD.ESD-26.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-28_TLF Pump House | ESD-28 | ESD 16 | TLF Pump House | ESD.ESD-28.ESD_STATUS | 0 | ESD.ESD-28.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-29_CENTRAL ESD | ESD-29 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-29.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1424 | Jabalpur | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1424 | Jabalpur | LP 01_BC-501A_BS VI HSD | LP 01 | TLF | BC-501A | BS VI HSD | SmartLoad-Dual.BC-501A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 02_BC-501B_BS VI HSD | LP 02 | TLF | BC-501B | BS VI HSD | SmartLoad-Dual.BC-501B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-501B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 03_BC-502A_BS VI MS | LP 03 | TLF | BC-502A | BS VI MS | SmartLoad-Dual.BC-502A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-502A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 04_BC-502B_BS VI HSD | LP 04 | TLF | BC-502B | BS VI HSD | SmartLoad-Dual.BC-502B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-502B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 05_BC-503A_BS VI MS | LP 05 | TLF | BC-503A | BS VI MS | SmartLoad-Dual.BC-503A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-503A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 06_BC-503B_BS VI HSD | LP 06 | TLF | BC-503B | BS VI HSD | SmartLoad-Dual.BC-503B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 07_BC-504A_BS VI MS | LP 07 | TLF | BC-504A | BS VI MS | SmartLoad-Dual.BC-504A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-504A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 08_BC-504B_BS VI HSD | LP 08 | TLF | BC-504B | BS VI HSD | SmartLoad-Dual.BC-504B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 09_BC-505A_BS VI MS | LP 09 | TLF | BC-505A | BS VI MS | SmartLoad-Dual.BC-505A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-505A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-505A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 10_BC-505B_BS VI HSD | LP 10 | TLF | BC-505B | BS VI HSD | SmartLoad-Dual.BC-505B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-505B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 11_BC-506A_BS VI MS | LP 11 | TLF | BC-506A | BS VI MS | SmartLoad-Dual.BC-506A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-506A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-506A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 12_BC-506B_BS VI HSD | LP 12 | TLF | BC-506B | BS VI HSD | SmartLoad-Dual.BC-506B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-506B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-506B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 13_BC-507A_BS VI MS | LP 13 | TLF | BC-507A | BS VI MS | SmartLoad-Dual.BC-507A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-507A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 14_BC-507B_BS VI HSD | LP 14 | TLF | BC-507B | BS VI HSD | SmartLoad-Dual.BC-507B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 15_BC-508A_BS VI MS | LP 15 | TLF | BC-508A | BS VI MS | SmartLoad-Dual.BC-508A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.BATCH_STATUS | 2 | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-508A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-508A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1424 | Jabalpur | LP 16_BC-508B_BS VI HSD | LP 16 | TLF | BC-508B | BS VI HSD | SmartLoad-Dual.BC-508B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.BATCH_STATUS | 2 | SmartLoad-Dual.BC-508B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-508B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1424 | Jabalpur | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1424 | Jabalpur | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-501A.PERMISSIVE_FROM_DNC_STATUS | 0
1424 | Jabalpur | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1424 | Jabalpur | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1424 | Jabalpur | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1424 | Jabalpur | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1424 | Jabalpur | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1424 | Jabalpur | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1424 | Jabalpur | Operability Index | PUMP.FWP-01.ON | 0 | PUMP.FWP-02.ON | 0 | PUMP.FWP-03.ON | 0 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.PT-01.PRESSURE |  | PressureTransmitter.PT-02.PRESSURE |  | PLC.GEPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1