## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1509 | Sholapur | TK-01_ETHANOL | TK-01 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | FALSE | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | FALSE | TANK.TK-01.HIGH_HIGH_LEVEL | FALSE | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | FALSE | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | FALSE | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | FALSE | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | FALSE | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | FALSE | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | FALSE | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | FALSE | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | FALSE | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | FALSE | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | FALSE | ROSOV-02 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-01.OPEN_STATUS | FALSE | DBBV-01 | MOV IL1 |  |  |  |  | MOV.DBBV-02.OPEN_STATUS | FALSE | DBBV-02 | MOV OL
1509 | Sholapur | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | FALSE | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | FALSE | TANK.TK-02.HIGH_HIGH_LEVEL | FALSE | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | FALSE | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | FALSE | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | FALSE | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | FALSE | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | FALSE | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | FALSE | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | FALSE | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | FALSE | ROSOV-03 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-04.OPEN_STATUS | FALSE | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | FALSE | ROSOV-04 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-04.OPEN_STATUS | FALSE | DBBV-04 | MOV IL1 |  |  |  |  | MOV.DBBV-05.OPEN_STATUS | FALSE | DBBV-05 | MOV OL
1509 | Sholapur | TK-03_ETHANOL | TK-03 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | FALSE | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | FALSE | TANK.TK-03.HIGH_HIGH_LEVEL | FALSE | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | FALSE | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | FALSE | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | FALSE | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | FALSE | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | FALSE | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | FALSE | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | FALSE | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | FALSE | ROSOV-05 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-06.OPEN_STATUS | FALSE | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | FALSE | ROSOV-06 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-07.OPEN_STATUS | FALSE | DBBV-07 | MOV IL1 |  |  |  |  | MOV.DBBV-08.OPEN_STATUS | FALSE | DBBV-08 | MOV OL
1509 | Sholapur | TK-04_SKO | TK-04 | AG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | FALSE | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | FALSE | TANK.TK-04.HIGH_HIGH_LEVEL | FALSE | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | FALSE | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | FALSE | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | FALSE | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | FALSE | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | FALSE | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | FALSE | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | FALSE | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | FALSE | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | FALSE | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | FALSE | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-09.OPEN_STATUS | FALSE | DBBV-09 | MOV IL1 |  |  |  |  | MOV.DBBV-10.OPEN_STATUS | FALSE | DBBV-10 | MOV OL
1509 | Sholapur | TK-05_SLOP | TK-05 | AG | SLOP | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | FALSE | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | FALSE | TANK.TK-05.HIGH_HIGH_LEVEL | FALSE | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | FALSE | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | FALSE | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | FALSE | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | FALSE | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | FALSE | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | FALSE | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | FALSE | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | FALSE | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | FALSE | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | FALSE | ROSOV-10 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-32.OPEN_STATUS | FALSE | DBBV-32 | MOV IL1 | MOV.DBBV-33.OPEN_STATUS | FALSE | DBBV-33 | MOV IL2 | MOV.DBBV-34.OPEN_STATUS | FALSE | DBBV-34 | MOV OL
1509 | Sholapur | TK-06_ETHANOL | TK-06 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | FALSE | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | FALSE | TANK.TK-06.HIGH_HIGH_LEVEL | FALSE | TK-06 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | FALSE | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | FALSE | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | FALSE | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | FALSE | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | FALSE | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | FALSE | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | FALSE | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | FALSE | ROSOV-11 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-12.OPEN_STATUS | FALSE | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | FALSE | ROSOV-12 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-35.OPEN_STATUS | FALSE | DBBV-35 | MOV IL1 |  |  |  |  | MOV.DBBV-36.OPEN_STATUS | FALSE | DBBV-36 | MOV OL
1509 | Sholapur | TK-07_BS VI MS | TK-07 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | FALSE | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | FALSE | TANK.TK-07.HIGH_HIGH_LEVEL | FALSE | TK-07 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | FALSE | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | FALSE | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | FALSE | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | FALSE | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | FALSE | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | FALSE | RDR-07 | RADAR | MOV.ROSOV-13.OPEN_STATUS | FALSE | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | FALSE | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | FALSE | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | FALSE | ROSOV-14 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-11.OPEN_STATUS | FALSE | DBBV-11 | MOV IL1 |  |  |  |  | MOV.DBBV-12.OPEN_STATUS | FALSE | DBBV-12 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-01.FIRE_ALARM | FALSE | RIMSEAL-01 | RIMSEAL | RIMSEAL.RIMSEAL-01.DETECTOR_FAULT | FALSE | RIMSEAL-01 | RIMSEAL
1509 | Sholapur | TK-08_BS VI MS | TK-08 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | FALSE | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | FALSE | TANK.TK-08.HIGH_HIGH_LEVEL | FALSE | TK-08 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | FALSE | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | FALSE | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | FALSE | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | FALSE | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | FALSE | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | FALSE | RDR-08 | RADAR | MOV.ROSOV-15.OPEN_STATUS | FALSE | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | FALSE | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-16.OPEN_STATUS | FALSE | ROSOV-16 | ROSOV OL | MOV.ROSOV-16.FAILED_TO_CLOSE | FALSE | ROSOV-16 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-14.OPEN_STATUS | FALSE | DBBV-14 | MOV IL1 |  |  |  |  | MOV.DBBV-15.OPEN_STATUS | FALSE | DBBV-15 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-02.FIRE_ALARM | FALSE | RIMSEAL-02 | RIMSEAL | RIMSEAL.RIMSEAL-02.DETECTOR_FAULT | FALSE | RIMSEAL-02 | RIMSEAL
1509 | Sholapur | TK-09_BS VI MS | TK-09 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | FALSE | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | FALSE | TANK.TK-09.HIGH_HIGH_LEVEL | FALSE | TK-09 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | FALSE | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | FALSE | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | FALSE | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | FALSE | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | FALSE | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | FALSE | RDR-09 | RADAR | MOV.ROSOV-17.OPEN_STATUS | FALSE | ROSOV-17 | ROSOV IL1 | MOV.ROSOV-17.FAILED_TO_CLOSE | FALSE | ROSOV-17 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-18.OPEN_STATUS | FALSE | ROSOV-18 | ROSOV OL | MOV.ROSOV-18.FAILED_TO_CLOSE | FALSE | ROSOV-18 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-17.OPEN_STATUS | FALSE | DBBV-17 | MOV IL1 |  |  |  |  | MOV.DBBV-18.OPEN_STATUS | FALSE | DBBV-18 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-03.FIRE_ALARM | FALSE | RIMSEAL-03 | RIMSEAL | RIMSEAL.RIMSEAL-03.DETECTOR_FAULT | FALSE | RIMSEAL-03 | RIMSEAL
1509 | Sholapur | TK-10_WATER | TK-10 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar | [6 empty] | TANK.TK-10.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-11_WATER | TK-11 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar | [6 empty] | TANK.TK-11.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-12_BS VI HSD | TK-12 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.HIGH_LEVEL | FALSE | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM | FALSE | TANK.TK-12.HIGH_HIGH_LEVEL | FALSE | TK-12 | Primary Radar | LEVELSWITCH.LSW-11.SWITCH_STATUS | FALSE | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_OK | FALSE | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_FAILED | FALSE | LSW-11 | VFT | LEVELSWITCH.RDR-11.SWITCH_STATUS | FALSE | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_OK | FALSE | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_FAILED | FALSE | RDR-11 | RADAR | MOV.ROSOV-21.OPEN_STATUS | FALSE | ROSOV-21 | ROSOV IL1 | MOV.ROSOV-21.FAILED_TO_CLOSE | FALSE | ROSOV-21 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-22.OPEN_STATUS | FALSE | ROSOV-22 | ROSOV OL | MOV.ROSOV-22.FAILED_TO_CLOSE | FALSE | ROSOV-22 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-23.OPEN_STATUS | FALSE | DBBV-23 | MOV IL1 |  |  |  |  | MOV.DBBV-24.OPEN_STATUS | FALSE | DBBV-24 | MOV OL
1509 | Sholapur | TK-13_BS VI HSD | TK-13 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.HIGH_LEVEL | FALSE | TK-13 | Primary Radar | TANK.TK-13.TANK_ALERT_ALARM | FALSE | TANK.TK-13.HIGH_HIGH_LEVEL | FALSE | TK-13 | Primary Radar | LEVELSWITCH.LSW-12.SWITCH_STATUS | FALSE | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_OK | FALSE | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_FAILED | FALSE | LSW-12 | VFT | LEVELSWITCH.RDR-12.SWITCH_STATUS | FALSE | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_OK | FALSE | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_FAILED | FALSE | RDR-12 | RADAR | MOV.ROSOV-23.OPEN_STATUS | FALSE | ROSOV-23 | ROSOV IL1 | MOV.ROSOV-23.FAILED_TO_CLOSE | FALSE | ROSOV-23 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-24.OPEN_STATUS | FALSE | ROSOV-24 | ROSOV OL | MOV.ROSOV-24.FAILED_TO_CLOSE | FALSE | ROSOV-24 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-26.OPEN_STATUS | FALSE | DBBV-26 | MOV IL1 |  |  |  |  | MOV.DBBV-27.OPEN_STATUS | FALSE | DBBV-27 | MOV OL
1509 | Sholapur | TK-14_BS VI HSD | TK-14 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | FALSE | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | FALSE | TANK.TK-14.HIGH_HIGH_LEVEL | FALSE | TK-14 | Primary Radar | LEVELSWITCH.LSW-13.SWITCH_STATUS | FALSE | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_OK | FALSE | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_FAILED | FALSE | LSW-13 | VFT | LEVELSWITCH.RDR-13.SWITCH_STATUS | FALSE | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_OK | FALSE | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_FAILED | FALSE | RDR-13 | RADAR | MOV.ROSOV-25.OPEN_STATUS | FALSE | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | FALSE | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-26.OPEN_STATUS | FALSE | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | FALSE | ROSOV-26 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-29.OPEN_STATUS | FALSE | DBBV-29 | MOV IL1 |  |  |  |  | MOV.DBBV-30.OPEN_STATUS | FALSE | DBBV-30 | MOV OL
1509 | Sholapur | TK-15_BS VI MS | TK-15 | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.HIGH_LEVEL | FALSE | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | FALSE | TANK.TK-15.HIGH_HIGH_LEVEL | FALSE | TK-15 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | FALSE | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | FALSE | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | FALSE | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | FALSE | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | FALSE | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | FALSE | RDR-10 | RADAR | MOV.ROSOV-19.OPEN_STATUS | FALSE | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | FALSE | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | FALSE | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | FALSE | ROSOV-20 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-20.OPEN_STATUS | FALSE | DBBV-20 | MOV IL1 |  |  |  |  | MOV.DBBV-21.OPEN_STATUS | FALSE | DBBV-21 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-04.FIRE_ALARM | FALSE | RIMSEAL-04 | RIMSEAL | RIMSEAL.RIMSEAL-04.DETECTOR_FAULT | FALSE | RIMSEAL-04 | RIMSEAL
1509 | Sholapur | TK-16_ETHANOL | TK-16 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar | [6 empty] | TANK.TK-16.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-17_ETHANOL | TK-17 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar | [6 empty] | TANK.TK-17.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-18_BS VI HSD | TK-18 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-18.LEVEL |  | TK-18 | Primary Radar | [6 empty] | TANK.TK-18.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-19_SKO | TK-19 | UG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-19.LEVEL |  | TK-19 | Primary Radar | [6 empty] | TANK.TK-19.TANK_ALERT_ALARM | FALSE
1509 | Sholapur | TK-20_BS VI MS | TK-20 | UG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-20.LEVEL |  | TK-20 | Primary Radar | [6 empty] | TANK.TK-20.TANK_ALERT_ALARM | FALSE

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1509 | Sholapur_M | TK-01_ETHANOL | TK-01 | AG | ETHANOL | TANK.TK-01.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | FALSE | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | FALSE | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | FALSE | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | FALSE | ROSOV-02 | ROSOV OL |  |  |  |  | MOV.DBBV-01.MAINTENANCE_STATUS | FALSE | DBBV-01 | MOV IL1 | [8 empty] | MOV.DBBV-02.MAINTENANCE_STATUS | FALSE | DBBV-02 | MOV OL
1509 | Sholapur_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | FALSE | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | FALSE | RDR-02 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | FALSE | ROSOV-03 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-04.MAINTENANCE_STATUS | FALSE | ROSOV-04 | ROSOV OL |  |  |  |  | MOV.DBBV-04.MAINTENANCE_STATUS | FALSE | DBBV-04 | MOV IL1 | [8 empty] | MOV.DBBV-05.MAINTENANCE_STATUS | FALSE | DBBV-05 | MOV OL
1509 | Sholapur_M | TK-03_ETHANOL | TK-03 | AG | ETHANOL | TANK.TK-03.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | FALSE | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | FALSE | RDR-03 | RADAR | MOV.ROSOV-05.MAINTENANCE_STATUS | FALSE | ROSOV-05 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-06.MAINTENANCE_STATUS | FALSE | ROSOV-06 | ROSOV OL |  |  |  |  | MOV.DBBV-07.MAINTENANCE_STATUS | FALSE | DBBV-07 | MOV IL1 | [8 empty] | MOV.DBBV-08.MAINTENANCE_STATUS | FALSE | DBBV-08 | MOV OL
1509 | Sholapur_M | TK-04_SKO | TK-04 | AG | SKO | TANK.TK-04.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | FALSE | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | FALSE | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | FALSE | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | FALSE | ROSOV-08 | ROSOV OL |  |  |  |  | MOV.DBBV-09.MAINTENANCE_STATUS | FALSE | DBBV-09 | MOV IL1 | [8 empty] | MOV.DBBV-10.MAINTENANCE_STATUS | FALSE | DBBV-10 | MOV OL
1509 | Sholapur_M | TK-05_SLOP | TK-05 | AG | SLOP | TANK.TK-05.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | FALSE | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | FALSE | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | FALSE | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | FALSE | ROSOV-10 | ROSOV OL |  |  |  |  | MOV.DBBV-32.MAINTENANCE_STATUS | FALSE | DBBV-32 | MOV IL1 | MOV.DBBV-33.MAINTENANCE_STATUS | FALSE | DBBV-33 | MOV IL2 |  |  |  |  | MOV.DBBV-34.MAINTENANCE_STATUS | FALSE | DBBV-34 | MOV OL
1509 | Sholapur_M | TK-06_ETHANOL | TK-06 | AG | ETHANOL | TANK.TK-06.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | FALSE | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | FALSE | RDR-06 | RADAR | MOV.ROSOV-11.MAINTENANCE_STATUS | FALSE | ROSOV-11 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-12.MAINTENANCE_STATUS | FALSE | ROSOV-12 | ROSOV OL |  |  |  |  | MOV.DBBV-35.MAINTENANCE_STATUS | FALSE | DBBV-35 | MOV IL1 | [8 empty] | MOV.DBBV-36.MAINTENANCE_STATUS | FALSE | DBBV-36 | MOV OL
1509 | Sholapur_M | TK-07_BS VI MS | TK-07 | AG | BS VI MS | TANK.TK-07.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | FALSE | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | FALSE | RDR-07 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | FALSE | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | FALSE | ROSOV-14 | ROSOV OL |  |  |  |  | MOV.DBBV-11.MAINTENANCE_STATUS | FALSE | DBBV-11 | MOV IL1 | [8 empty] | MOV.DBBV-12.MAINTENANCE_STATUS | FALSE | DBBV-12 | MOV OL
1509 | Sholapur_M | TK-08_BS VI MS | TK-08 | AG | BS VI MS | TANK.TK-08.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | FALSE | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | FALSE | RDR-08 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | FALSE | ROSOV-15 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-16.MAINTENANCE_STATUS | FALSE | ROSOV-16 | ROSOV OL |  |  |  |  | MOV.DBBV-14.MAINTENANCE_STATUS | FALSE | DBBV-14 | MOV IL1 | [8 empty] | MOV.DBBV-15.MAINTENANCE_STATUS | FALSE | DBBV-15 | MOV OL
1509 | Sholapur_M | TK-09_BS VI MS | TK-09 | AG | BS VI MS | TANK.TK-09.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | FALSE | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | FALSE | RDR-09 | RADAR | MOV.ROSOV-17.MAINTENANCE_STATUS | FALSE | ROSOV-17 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-18.MAINTENANCE_STATUS | FALSE | ROSOV-18 | ROSOV OL |  |  |  |  | MOV.DBBV-17.MAINTENANCE_STATUS | FALSE | DBBV-17 | MOV IL1 | [8 empty] | MOV.DBBV-18.MAINTENANCE_STATUS | FALSE | DBBV-18 | MOV OL
1509 | Sholapur_M | TK-12_BS VI HSD | TK-12 | AG | BS VI HSD | TANK.TK-12.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-11.MAINTENANCE_STATUS | FALSE | LSW-11 | VFT | LEVELSWITCH.RDR-11.MAINTENANCE_STATUS | FALSE | RDR-11 | RADAR | MOV.ROSOV-21.MAINTENANCE_STATUS | FALSE | ROSOV-21 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-22.MAINTENANCE_STATUS | FALSE | ROSOV-22 | ROSOV OL |  |  |  |  | MOV.DBBV-23.MAINTENANCE_STATUS | FALSE | DBBV-23 | MOV IL1 | [8 empty] | MOV.DBBV-24.MAINTENANCE_STATUS | FALSE | DBBV-24 | MOV OL
1509 | Sholapur_M | TK-13_BS VI HSD | TK-13 | AG | BS VI HSD | TANK.TK-13.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-12.MAINTENANCE_STATUS | FALSE | LSW-12 | VFT | LEVELSWITCH.RDR-12.MAINTENANCE_STATUS | FALSE | RDR-12 | RADAR | MOV.ROSOV-23.MAINTENANCE_STATUS | FALSE | ROSOV-23 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-24.MAINTENANCE_STATUS | FALSE | ROSOV-24 | ROSOV OL |  |  |  |  | MOV.DBBV-26.MAINTENANCE_STATUS | FALSE | DBBV-26 | MOV IL1 | [8 empty] | MOV.DBBV-27.MAINTENANCE_STATUS | FALSE | DBBV-27 | MOV OL
1509 | Sholapur_M | TK-14_BS VI HSD | TK-14 | AG | BS VI HSD | TANK.TK-14.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-13.MAINTENANCE_STATUS | FALSE | LSW-13 | VFT | LEVELSWITCH.RDR-13.MAINTENANCE_STATUS | FALSE | RDR-13 | RADAR | MOV.ROSOV-25.MAINTENANCE_STATUS | FALSE | ROSOV-25 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-26.MAINTENANCE_STATUS | FALSE | ROSOV-26 | ROSOV OL |  |  |  |  | MOV.DBBV-29.MAINTENANCE_STATUS | FALSE | DBBV-29 | MOV IL1 | [8 empty] | MOV.DBBV-30.MAINTENANCE_STATUS | FALSE | DBBV-30 | MOV OL
1509 | Sholapur_M | TK-15_BS VI MS | TK-15 | AG | BS VI MS | TANK.TK-15.MAINTENANCE_STATUS | FALSE | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | FALSE | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | FALSE | RDR-10 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | FALSE | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | FALSE | ROSOV-20 | ROSOV OL |  |  |  |  | MOV.DBBV-20.MAINTENANCE_STATUS | FALSE | DBBV-20 | MOV IL1 | [8 empty] | MOV.DBBV-21.MAINTENANCE_STATUS | FALSE | DBBV-21 | MOV OL
1509 | Sholapur_M | TK-18_BS VI HSD | TK-18 | UG | BS VI HSD | TANK.TK-18.MAINTENANCE_STATUS | FALSE
1509 | Sholapur_M | TK-19_SKO | TK-19 | UG | SKO | TANK.TK-19.MAINTENANCE_STATUS | FALSE
1509 | Sholapur_M | TK-20_BS VI MS | TK-20 | UG | BS VI MS | TANK.TK-20.MAINTENANCE_STATUS | FALSE

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1509 | Sholapur | PMP-07_ITT_MS_PMP1_Both | PMP-07 | ITT_MS_PMP1 | ITT PUMP HOUSE | Both | PUMP.PMP-07.ON | FALSE | PUMP.PMP-07.REMOTE_STATUS | TRUE | PUMP.PMP-07.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-08_ITT_SKO_PMP2_Both | PMP-08 | ITT_SKO_PMP2 | ITT PUMP HOUSE | Both | PUMP.PMP-08.ON | FALSE | PUMP.PMP-08.REMOTE_STATUS | TRUE | PUMP.PMP-08.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-09_ITT_SKO_PMP3_Both | PMP-09 | ITT_SKO_PMP3 | ITT PUMP HOUSE | Both | PUMP.PMP-09.ON | FALSE | PUMP.PMP-09.REMOTE_STATUS | TRUE | PUMP.PMP-09.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-24_ADTV-PMP-1 POWER_TL | PMP-24 | ADTV-PMP-1 POWER | TLF PUMP HOUSE | TL | PUMP.PMP-24.ON | FALSE | PUMP.PMP-24.REMOTE_STATUS | TRUE | PUMP.PMP-24.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-25_ADTV-PMP-2 POWER_TL | PMP-25 | ADTV-PMP-2 POWER | TLF PUMP HOUSE | TL | PUMP.PMP-25.ON | FALSE | PUMP.PMP-25.REMOTE_STATUS | TRUE | PUMP.PMP-25.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-26_ADTV-PMP-1 TURBO_TL | PMP-26 | ADTV-PMP-1 TURBO | TLF PUMP HOUSE | TL | PUMP.PMP-26.ON | FALSE | PUMP.PMP-26.REMOTE_STATUS | TRUE | PUMP.PMP-26.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-27_ADTV-PMP-2 TURBO_TL | PMP-27 | ADTV-PMP-2 TURBO | TLF PUMP HOUSE | TL | PUMP.PMP-27.ON | FALSE | PUMP.PMP-27.REMOTE_STATUS | TRUE | PUMP.PMP-27.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-28_ADTV-PMP-1 BLUEDYE_TL | PMP-28 | ADTV-PMP-1 BLUEDYE | TLF PUMP HOUSE | TL | PUMP.PMP-28.ON | FALSE | PUMP.PMP-28.REMOTE_STATUS | TRUE | PUMP.PMP-28.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-29_ADTV-PMP-2 BLUEDYE_TL | PMP-29 | ADTV-PMP-2 BLUEDYE | TLF PUMP HOUSE | TL | PUMP.PMP-29.ON | FALSE | PUMP.PMP-29.REMOTE_STATUS | TRUE | PUMP.PMP-29.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-31_TLF_MS_PMP1_TL | PMP-31 | TLF_MS_PMP1 | TLF PUMP HOUSE | TL | PUMP.PMP-31.ON | FALSE | PUMP.PMP-31.REMOTE_STATUS | TRUE | PUMP.PMP-31.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-32_TLF_MS_PMP2_TL | PMP-32 | TLF_MS_PMP2 | TLF PUMP HOUSE | TL | PUMP.PMP-32.ON | FALSE | PUMP.PMP-32.REMOTE_STATUS | TRUE | PUMP.PMP-32.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-33_TLF_MS_PMP3_TL | PMP-33 | TLF_MS_PMP3 | TLF PUMP HOUSE | TL | PUMP.PMP-33.ON | FALSE | PUMP.PMP-33.REMOTE_STATUS | TRUE | PUMP.PMP-33.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-34_TLF_HSD_PMP1_TL | PMP-34 | TLF_HSD_PMP1 | TLF PUMP HOUSE | TL | PUMP.PMP-34.ON | FALSE | PUMP.PMP-34.REMOTE_STATUS | TRUE | PUMP.PMP-34.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-35_TLF_HSD_PMP2_TL | PMP-35 | TLF_HSD_PMP2 | TLF PUMP HOUSE | TL | PUMP.PMP-35.ON | FALSE | PUMP.PMP-35.REMOTE_STATUS | TRUE | PUMP.PMP-35.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-36_TLF_HSD_PMP3_TL | PMP-36 | TLF_HSD_PMP3 | TLF PUMP HOUSE | TL | PUMP.PMP-36.ON | FALSE | PUMP.PMP-36.REMOTE_STATUS | TRUE | PUMP.PMP-36.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-37_TLF_ETH_PMP_TK14_TL | PMP-37 | TLF_ETH_PMP_TK14 | At ETHANOL UG TK 14 | TL | PUMP.PMP-37.ON | FALSE | PUMP.PMP-37.REMOTE_STATUS | TRUE | PUMP.PMP-37.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-38_TLF_ETH_PMP_TK15_TL | PMP-38 | TLF_ETH_PMP_TK15 | At ETHANOL UG TK 15 | TL | PUMP.PMP-38.ON | FALSE | PUMP.PMP-38.REMOTE_STATUS | TRUE | PUMP.PMP-38.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-39_TLF_SKO_PMP1_TL | PMP-39 | TLF_SKO_PMP1 | TLF PUMP HOUSE | TL | PUMP.PMP-39.ON | FALSE | PUMP.PMP-39.REMOTE_STATUS | TRUE | PUMP.PMP-39.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-40_TLF_SKO_PMP2_TL | PMP-40 | TLF_SKO_PMP2 | TLF PUMP HOUSE | TL | PUMP.PMP-40.ON | FALSE | PUMP.PMP-40.REMOTE_STATUS | TRUE | PUMP.PMP-40.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-45_TWD_MS_PMP1_WL | PMP-45 | TWD_MS_PMP1 | TWD PUMP HOUSE | WL | PUMP.PMP-45.ON | FALSE | PUMP.PMP-45.REMOTE_STATUS | TRUE | PUMP.PMP-45.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-46_TWD_MS_PMP2_WL | PMP-46 | TWD_MS_PMP2 | TWD PUMP HOUSE | WL | PUMP.PMP-46.ON | FALSE | PUMP.PMP-46.REMOTE_STATUS | TRUE | PUMP.PMP-46.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-47_TWD_ETH_PMP1_WL | PMP-47 | TWD_ETH_PMP1 | TWD PUMP HOUSE | WL | PUMP.PMP-47.ON | FALSE | PUMP.PMP-47.REMOTE_STATUS | TRUE | PUMP.PMP-47.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-48_TWD_ETH_PMP2_WL | PMP-48 | TWD_ETH_PMP2 | TWD PUMP HOUSE | WL | PUMP.PMP-48.ON | FALSE | PUMP.PMP-48.REMOTE_STATUS | TRUE | PUMP.PMP-48.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-49_TWD_HSD_PMP1_WL | PMP-49 | TWD_HSD_PMP1 | TWD PUMP HOUSE | WL | PUMP.PMP-49.ON | FALSE | PUMP.PMP-49.REMOTE_STATUS | TRUE | PUMP.PMP-49.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-50_TWD_HSD_PMP2_WL | PMP-50 | TWD_HSD_PMP2 | TWD PUMP HOUSE | WL | PUMP.PMP-50.ON | FALSE | PUMP.PMP-50.REMOTE_STATUS | TRUE | PUMP.PMP-50.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-51_TLF_ETH_PMP1_AGTK_TL | PMP-51 | TLF_ETH_PMP1_AGTK | ITT/ETH PUMP HOUSE | TL | PUMP.PMP-51.ON | FALSE | PUMP.PMP-51.REMOTE_STATUS | TRUE | PUMP.PMP-51.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-52_TLF_ETH_PMP2_AGTK_TL | PMP-52 | TLF_ETH_PMP2_AGTK | ITT/ETH PUMP HOUSE | TL | PUMP.PMP-52.ON | FALSE | PUMP.PMP-52.REMOTE_STATUS | TRUE | PUMP.PMP-52.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PMP-53_TLF_ETH_PMP3_AGTK_TL | PMP-53 | TLF_ETH_PMP3_AGTK | ITT/ETH PUMP HOUSE | TL | PUMP.PMP-53.ON | FALSE | PUMP.PMP-53.REMOTE_STATUS | TRUE | PUMP.PMP-53.MAINTENANCE_STATUS | FALSE

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1509 | Sholapur | FWP-01_Water_DISPATCH | FWP-01 | Water | HP | DISPATCH | PUMP.FWP-01.ON | FALSE | PUMP.FWP-01.REMOTE_STATUS | TRUE | PUMP.FWP-01.MAINTENANCE_STATUS | FALSE | PUMP.FWP-01.FAILED_TO_START_MAIN1 | FALSE | PUMP.FWP-01.FAILED_TO_START_MAIN2 | FALSE |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY | FALSE | PUMP.FWP-01.PUMP_TRIPPED | FALSE |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | FALSE
1509 | Sholapur | FWP-02_Water_DISPATCH | FWP-02 | Water | HP | DISPATCH | PUMP.FWP-02.ON | FALSE | PUMP.FWP-02.REMOTE_STATUS | TRUE | PUMP.FWP-02.MAINTENANCE_STATUS | FALSE | PUMP.FWP-02.FAILED_TO_START_MAIN1 | FALSE | PUMP.FWP-02.FAILED_TO_START_MAIN2 | FALSE |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY | FALSE | PUMP.FWP-02.PUMP_TRIPPED | FALSE |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | FALSE
1509 | Sholapur | FWP-03_Water_DISPATCH | FWP-03 | Water | HP | DISPATCH | PUMP.FWP-03.ON | FALSE | PUMP.FWP-03.REMOTE_STATUS | TRUE | PUMP.FWP-03.MAINTENANCE_STATUS | FALSE | PUMP.FWP-03.FAILED_TO_START_MAIN1 | FALSE | PUMP.FWP-03.FAILED_TO_START_MAIN2 | FALSE |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY | FALSE | PUMP.FWP-03.PUMP_TRIPPED | FALSE |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | FALSE
1509 | Sholapur | JCY-01_Water_DISPATCH | JCY-01 | Water | HP | DISPATCH | PUMP.JCY-01.ON | FALSE | PUMP.JCY-01.REMOTE_STATUS | TRUE | PUMP.JCY-01.MAINTENANCE_STATUS | FALSE | PUMP.JCY-01.FAILED_TO_START_MAIN1 | FALSE |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | FALSE | PUMP.JCY-01.PUMP_TRIPPED | FALSE
1509 | Sholapur | JCY-02_Water_DISPATCH | JCY-02 | Water | HP | DISPATCH | PUMP.JCY-02.ON | FALSE | PUMP.JCY-02.REMOTE_STATUS | TRUE | PUMP.JCY-02.MAINTENANCE_STATUS | FALSE | PUMP.JCY-02.FAILED_TO_START_MAIN1 | FALSE |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | FALSE | PUMP.JCY-02.PUMP_TRIPPED | FALSE
1509 | Sholapur | PT-05 _WP_Near FE shed | PT-05 | WP | PT | Near FE shed |  |  |  |  | PressureTransmitter.PT-05.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PT-06_WP_Near tank 5 | PT-06 | WP | PT | Near tank 5 |  |  |  |  | PressureTransmitter.PT-06.MAINTENANCE_STATUS | FALSE
1509 | Sholapur | PT-07_WP_Near tank 101D | PT-07 | WP | PT | Near tank 101D |  |  |  |  | PressureTransmitter.PT-07.MAINTENANCE_STATUS | FALSE

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1509 | Sholapur | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | FALSE | UPS.UPS-01.LOAD_ON_UPS | FALSE | UPS.UPS-01.MAIN_AC_FAIL | FALSE
1509 | Sholapur | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | FALSE | UPS.UPS-02.LOAD_ON_UPS | FALSE | UPS.UPS-02.MAIN_AC_FAIL | FALSE
1509 | Sholapur | UPS-03_Control Room | UPS-03 | Control Room |  |  | UPS.UPS-03.LOW_BATTERY | FALSE | UPS.UPS-03.UPS_ON | FALSE | UPS.UPS-03.MAIN_AC_FAIL | FALSE
1509 | Sholapur | UPS-04_Control Room | UPS-04 | Control Room |  |  | UPS.UPS-04.LOW_BATTERY | FALSE | UPS.UPS-04.UPS_ON | FALSE | UPS.UPS-04.MAIN_AC_FAIL | FALSE

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1509 | Sholapur | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | TRUE | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | TRUE | TASPLC | PLCB
1509 | Sholapur | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | TRUE | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | TRUE | SFTPLC | PLCB | PLC.SFTPLC.PLCAB_FAIL_SAFE_STATUS | FALSE | SFTPLC | PLCA |  |  |  |  | PLC.SFTPLC.PLCA_COMM_OK | FALSE | SFTPLC | PLCA | PLC.SFTPLC.PLCB_COMM_OK | FALSE | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1509 | Sholapur | HDS-01_OPENPATH_TANK - 05 | HDS-01 | OPENPATH | TANK - 05 | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-01.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-01.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-02_OPENPATH_ITT PUMP HOUSE | HDS-02 | OPENPATH | ITT PUMP HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-02.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-02.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-03_OPENPATH_TLF PUMP HOUSE | HDS-03 | OPENPATH | TLF PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-03.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-03.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-04_OPENPATH_NEAR TK-101A AND 101C | HDS-04 | OPENPATH | NEAR TK-101A AND 101C | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-04.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-04.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-05_OPENPATH_TWD PUMP HOUSE | HDS-05 | OPENPATH | TWD PUMP HOUSE | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-05.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-05.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-06_OPENPATH_OMC PLT PUMP HOUSE | HDS-06 | OPENPATH | OMC PLT PUMP HOUSE | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-06.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-06.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-07_OPENPATH_TK-101D | HDS-07 | OPENPATH | TK-101D | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-07.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-07.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-08_FIXEDTYPE_TK-101D | HDS-08 | FIXEDTYPE | TK-101D | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-08.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-08.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-09_FIXEDTYPE_TK-05 | HDS-09 | FIXEDTYPE | TK-05 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-09.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-09.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-10_FIXEDTYPE_TK-101A | HDS-10 | FIXEDTYPE | TK-101A | GDS.HDS-10.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-10.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-10.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-10.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-10.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-11_FIXEDTYPE_TK-101C | HDS-11 | FIXEDTYPE | TK-101C | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-11.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-11.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-12_FIXEDTYPE_TK-101B | HDS-12 | FIXEDTYPE | TK-101B | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-12.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-12.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-13_FIXEDTYPE_TLF PUMP HOUSE_FIXED | HDS-13 | FIXEDTYPE | TLF PUMP HOUSE_FIXED | GDS.HDS-13.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-13.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-13.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-13.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-13.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-14_FIXEDTYPE_ITT/ETH TLF PUMP HOUSE_FIXED | HDS-14 | FIXEDTYPE | ITT/ETH TLF PUMP HOUSE_FIXED | GDS.HDS-14.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-14.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-14.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-14.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-14.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-15_FIXEDTYPE_TWD PUMP HOUSE | HDS-15 | FIXEDTYPE | TWD PUMP HOUSE | GDS.HDS-15.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-15.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-15.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-15.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-15.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-16_FIXEDTYPE_PLT PUMP HOUSE | HDS-16 | FIXEDTYPE | PLT PUMP HOUSE | GDS.HDS-16.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-16.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-16.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-16.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-16.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-17_FIXEDTYPE_NEAR TK-03 | HDS-17 | FIXEDTYPE | NEAR TK-03 | GDS.HDS-17.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-17.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-17.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-17.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-17.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-39_FIXEDTYPE_Near Tank no.1 | HDS-39 | FIXEDTYPE | Near Tank no.1 | GDS.HDS-39.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-39.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-39.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-39.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-39.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE
1509 | Sholapur | HDS-40_FIXEDTYPE_Near VRU | HDS-40 | FIXEDTYPE | Near VRU | GDS.HDS-40.HYDROCARBON_40_PCT_LEL | FALSE | GDS.HDS-40.HYDROCARBON_20_PCT_LEL | FALSE | GDS.HDS-40.CRITICAL_FAULT_ALARM | FALSE | GDS.HDS-40.MISALIGNMENT_FAULT_ALARM | FALSE | GDS.HDS-40.MAINTENANCE_CALL | FALSE | PLC.SFTPLC.EEFFECT_HOOTER_FOR_HC_CR | FALSE

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1509 | Sholapur | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-05 | DRAINVALVE.DV-05.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-06 | DRAINVALVE.DV-06.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-07 | DRAINVALVE.DV-07.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE
1509 | Sholapur | DV-08 | DRAINVALVE.DV-08.DRAIN_VALVE_STATUS | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | FALSE

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1509 | Sholapur | EntryGate | GATE.EntryGate.OPEN_STATUS | FALSE | GATE.EntryGate.REMOTE_STATUS | TRUE
1509 | Sholapur | ExitGate | GATE.ExitGate.OPEN_STATUS | FALSE | GATE.ExitGate.REMOTE_STATUS | TRUE

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1509 | Sholapur | HOOTER_HOOTER_FIELD_1 | HOOTER | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_2 | HOOTER | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_3 | HOOTER | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_4 | HOOTER | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_5 | HOOTER | HOOTER_FIELD_5 | PLC.SFTPLC.HOOTER_FIELD_5 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_6 | HOOTER | HOOTER_FIELD_6 | PLC.SFTPLC.HOOTER_FIELD_6 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_7 | HOOTER | HOOTER_FIELD_7 | PLC.SFTPLC.HOOTER_FIELD_7 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_8 | HOOTER | HOOTER_FIELD_8 | PLC.SFTPLC.HOOTER_FIELD_8 | FALSE
1509 | Sholapur | HOOTER_HOOTER_FIELD_9 | HOOTER | HOOTER_FIELD_9 | PLC.SFTPLC.HOOTER_FIELD_9 | FALSE

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1509 | Sholapur | ESD-01_SECURITY ROOM | ESD-01 | ESDPB-01 | SECURITY ROOM | ESD.ESD-01.ESD_STATUS | FALSE | ESD.ESD-01.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-02_OUTSIDE CONTROL ROOM | ESD-02 | ESDPB-02 | OUTSIDE CONTROL ROOM | ESD.ESD-02.ESD_STATUS | FALSE | ESD.ESD-02.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-03_TLF GANTRY AREA | ESD-03 | ESDPB-03 | TLF GANTRY AREA | ESD.ESD-03.ESD_STATUS | FALSE | ESD.ESD-03.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-04_TLF PUMP HOUSE | ESD-04 | ESDPB-04 | TLF PUMP HOUSE | ESD.ESD-04.ESD_STATUS | FALSE | ESD.ESD-04.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-05_TWD PUMP HOUSE | ESD-05 | ESDPB-05 | TWD PUMP HOUSE | ESD.ESD-05.ESD_STATUS | FALSE | ESD.ESD-05.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-06_B/W TANK 01 & 03 | ESD-06 | ESDPB-06 | B/W TANK 01 & 03 | ESD.ESD-06.ESD_STATUS | FALSE | ESD.ESD-06.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-07_NEAR TANK 04 | ESD-07 | ESDPB-07 | NEAR TANK 04 | ESD.ESD-07.ESD_STATUS | FALSE | ESD.ESD-07.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-08_NEAR TANK 101C | ESD-08 | ESDPB-08 | NEAR TANK 101C | ESD.ESD-08.ESD_STATUS | FALSE | ESD.ESD-08.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-09_NEAR TANK 102A/B DYKE VALVE | ESD-09 | ESDPB-09 | NEAR TANK 102A/B DYKE VALVE | ESD.ESD-09.ESD_STATUS | FALSE | ESD.ESD-09.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-10_NEAR TANK 101D | ESD-10 | ESDPB-10 | NEAR TANK 101D | ESD.ESD-10.ESD_STATUS | FALSE | ESD.ESD-10.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-11_OMC PLT PUMP HOUSE | ESD-11 | ESDPB-11 | OMC PLT PUMP HOUSE | ESD.ESD-11.ESD_STATUS | FALSE | ESD.ESD-11.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-12_INSIDE CONTROL ROOM | ESD-12 | ESDPB-12 | INSIDE CONTROL ROOM | ESD.ESD-12.ESD_STATUS | FALSE | ESD.ESD-12.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-13_AT LIC's ROOM | ESD-13 | ESDPB-13 | AT LIC's ROOM | ESD.ESD-13.ESD_STATUS | FALSE | ESD.ESD-13.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-16_CENTRAL ESD | ESD-16 | ESD-CENTRAL | CENTRAL ESD | ESD.ESD-16.ESD_STATUS | FALSE |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-17_PIPELINE ESD | ESD-17 | ESD-PIPELINE | PIPELINE ESD | ESD.ESD-17.ESD_STATUS | FALSE |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-18_RAILWAY SIDEING ESD | ESD-18 | ESDPB-18 | RAILWAY SIDEING ESD | ESD.ESD-18.ESD_STATUS | FALSE | ESD.ESD-18.MAINTENANCE_STATUS | FALSE | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-BPCL_BPCL CENTRAL ESD | ESD-BPCL | ESD-BPCL | BPCL CENTRAL ESD | ESD.ESD-BPCL.ESD_STATUS | FALSE |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-IOCL_IOCL CENTRAL ESD | ESD-IOCL | ESD-IOCL | IOCL CENTRAL ESD | ESD.ESD-IOCL.ESD_STATUS | FALSE |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE
1509 | Sholapur | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | FALSE |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | FALSE | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | FALSE | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | FALSE | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | FALSE | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | FALSE | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | FALSE

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1509 | Sholapur | LP 01_BC-01-LP01_BS VI MS | LP 01 | TLF | BC-01-LP01 | BS VI MS | SmartLoad-Dual.BC-01-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-01-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-01-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-01-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-01-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-01-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-01-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-01-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-01-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-01-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-01-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-01-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-01-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-01-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 02_BC-01-LP02_BS VI HSD | LP 02 | TLF | BC-01-LP02 | BS VI HSD | SmartLoad-Dual.BC-01-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-01-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-01-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-01-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-01-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-01-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-01-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-01-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-01-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 03_BC-02-LP01_BS VI MS | LP 03 | TLF | BC-02-LP01 | BS VI MS | SmartLoad-Dual.BC-02-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-02-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-02-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-02-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-02-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-02-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-02-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-02-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-02-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-02-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-02-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-02-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-02-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-02-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 04_BC-02-LP02_BS VI HSD | LP 04 | TLF | BC-02-LP02 | BS VI HSD | SmartLoad-Dual.BC-02-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-02-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-02-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-02-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-02-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-02-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-02-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-02-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-02-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 05_BC-03-LP01_BS VI MS | LP 05 | TLF | BC-03-LP01 | BS VI MS | SmartLoad-Dual.BC-03-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-03-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-03-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-03-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-03-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-03-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-03-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-03-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-03-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-03-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-03-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-03-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-03-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-03-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 06_BC-03-LP02_BS VI HSD | LP 06 | TLF | BC-03-LP02 | BS VI HSD | SmartLoad-Dual.BC-03-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-03-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-03-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-03-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-03-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-03-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-03-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-03-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-03-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 07_BC-04-LP01_BS VI MS | LP 07 | TLF | BC-04-LP01 | BS VI MS | SmartLoad-Dual.BC-04-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-04-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-04-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-04-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-04-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-04-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-04-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-04-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-04-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-04-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-04-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-04-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-04-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-04-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 08_BC-04-LP02_BS VI HSD | LP 08 | TLF | BC-04-LP02 | BS VI HSD | SmartLoad-Dual.BC-04-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-04-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-04-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-04-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-04-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-04-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-04-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-04-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-04-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 09_BC-05-LP01_BS VI HSD | LP 09 | TLF | BC-05-LP01 | BS VI HSD | SmartLoad-Dual.BC-05-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-05-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-05-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-05-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-05-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-05-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-05-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-05-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-05-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-05-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-05-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-05-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-05-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-05-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 10_BC-05-LP02_BS VI HSD | LP 10 | TLF | BC-05-LP02 | BS VI HSD | SmartLoad-Dual.BC-05-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-05-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-05-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-05-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-05-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-05-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-05-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-05-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-05-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 11_BC-BLUE-DYE_SKO | LP 11 | TLF | BC-BLUE-DYE | SKO | SmartLoad-Single.BC-BLUE-DYE.EARTH_ALARM_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.NO_FLOW_ALARM_STATUS_M1 | FALSE |  |  | SmartLoad-Single.BC-BLUE-DYE.LOW_FLOW_ALARM_STATUS_M1 | FALSE |  |  | SmartLoad-Single.BC-BLUE-DYE.HIGH_FLOW_ALARM_STATUS_M1 | FALSE |  |  | SmartLoad-Single.BC-BLUE-DYE.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Single.BC-BLUE-DYE.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Single.BC-BLUE-DYE.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.BATCH_STATUS | 2 | SmartLoad-Single.BC-BLUE-DYE.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Single.BC-BLUE-DYE.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Single.BC-BLUE-DYE.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 12_BC-06-LP01_BS VI MS | LP 12 | TLF | BC-06-LP01 | BS VI MS | SmartLoad-Dual.BC-06-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-06-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-06-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-06-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-06-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-06-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-06-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-06-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-06-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-06-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-06-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-06-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-06-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-06-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 13_BC-06-LP02_BS VI HSD | LP 13 | TLF | BC-06-LP02 | BS VI HSD | SmartLoad-Dual.BC-06-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-06-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-06-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-06-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-06-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-06-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-06-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-06-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-06-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 14_BC-07-LP01_BS VI MS | LP 14 | TLF | BC-07-LP01 | BS VI MS | SmartLoad-Dual.BC-07-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-07-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-07-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-07-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-07-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-07-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-07-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-07-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-07-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-07-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-07-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-07-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-07-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-07-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 15_BC-07-LP02_BS VI HSD | LP 15 | TLF | BC-07-LP02 | BS VI HSD | SmartLoad-Dual.BC-07-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-07-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-07-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-07-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-07-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-07-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-07-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-07-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-07-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 16_BC-08-LP01_BS VI MS | LP 16 | TLF | BC-08-LP01 | BS VI MS | SmartLoad-Dual.BC-08-LP01.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.NO_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-08-LP01.NO_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-08-LP01.LOW_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-08-LP01.LOW_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-08-LP01.HIGH_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-08-LP01.HIGH_FLOW_ALARM_STATUS_M2 | FALSE | SmartLoad-Dual.BC-08-LP01.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-08-LP01.METER_OVERRUN_ALARM_STATUS_M1 | FALSE | SmartLoad-Dual.BC-08-LP01.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.BATCH_STATUS | 2 | SmartLoad-Dual.BC-08-LP01.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-08-LP01.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | FALSE | SmartLoad-Dual.BC-08-LP01.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-08-LP01.BCU_C1_TOTALIZER_MISMATCH_ALARM | FALSE | SmartLoad-Dual.BC-08-LP01.BCU_C2_TOTALIZER_MISMATCH_ALARM | FALSE
1509 | Sholapur | LP 17_BC-08-LP02_BS VI HSD | LP 17 | TLF | BC-08-LP02 | BS VI HSD | SmartLoad-Dual.BC-08-LP02.EARTH_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.NO_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-08-LP02.LOW_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-08-LP02.HIGH_FLOW_ALARM_STATUS_M3 | FALSE |  |  | SmartLoad-Dual.BC-08-LP02.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-08-LP02.METER_OVERRUN_ALARM_STATUS_M3 | FALSE | SmartLoad-Dual.BC-08-LP02.BLEND_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.BLEND_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.ADDITIVE_OVERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.ADDITIVE_UNDERDOSE_ALARM_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.BATCH_STATUS | 2 | SmartLoad-Dual.BC-08-LP02.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | FALSE |  |  | SmartLoad-Dual.BC-08-LP02.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | FALSE | SmartLoad-Dual.BC-08-LP02.BCU_C3_TOTALIZER_MISMATCH_ALARM | FALSE

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1509 | Sholapur | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | FALSE
1509 | Sholapur | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01-LP01.PERMISSIVE_FROM_DNC_STATUS | FALSE
1509 | Sholapur | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | FALSE

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1509 | Sholapur | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE
1509 | Sholapur | WATER Level below Ref. Volume | PLC.SFTPLC.CAUSE_WATERTK_VOL_BELOW_90PCT | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE
1509 | Sholapur | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | FALSE | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | FALSE |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | FALSE
1509 | Sholapur | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | FALSE

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1509 | Sholapur | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | FALSE

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1509 | Sholapur | Operability Index | PUMP.FWP-01.ON | FALSE | PUMP.FWP-02.ON | FALSE | PUMP.FWP-03.ON | FALSE | PUMP.JCY-01.ON | FALSE | PUMP.JCY-02.ON | FALSE | PressureTransmitter.PT-05.PRESSURE |  | PressureTransmitter.PT-07.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | FALSE | PUMP.JCY-01.REMOTE_STATUS | TRUE | PUMP.JCY-01.AUTO_STATUS | TRUE | PUMP.JCY-02.REMOTE_STATUS | TRUE | PUMP.JCY-02.AUTO_STATUS | TRUE