## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1588 | Vashi | TK-101_ETHANOL | TK-101 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-101.LEVEL |  | TK-101 | Primary Radar |  |  | TANK.TK-101.TANK_ALERT_ALARM | 0 | TANK.TK-101.HIGH_LEVEL | 0 | TK-101 | Primary Radar | TANK.TK-101.HIGH_HIGH_LEVEL | 0 | TK-101 | Primary Radar | LEVELSWITCH.VIB TK101.SWITCH_STATUS | 0 | VIB TK101 | VFT | LEVELSWITCH.VIB TK101.PROOF_TEST_OK | 0 | VIB TK101 | VFT | LEVELSWITCH.VIB TK101.PROOF_TEST_FAILED | 0 | VIB TK101 | VFT | LEVELSWITCH.RDR TK101.SWITCH_STATUS | 0 | RDR TK101 | RADAR | LEVELSWITCH.RDR TK101.PROOF_TEST_OK | 0 | RDR TK101 | RADAR | LEVELSWITCH.RDR TK101.PROOF_TEST_FAILED | 0 | RDR TK101 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_OPEN | 0 | ROSOV-02 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-01.OPEN_STATUS | 0 | DBBV-01 | MOV IL1 | MOV.DBBV-03.OPEN_STATUS | 0 | DBBV-03 | MOV IL2 | MOV.DBBV-02.OPEN_STATUS | 0 | DBBV-02 | MOV OL | MOV.DBBV-04.CLOSE_STATUS | 0 | DBBV-04 | MOV OL1
1588 | Vashi | TK-102_SLOP | TK-102 | AG | SLOP | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-102.LEVEL |  | TK-102 | Primary Radar |  |  | TANK.TK-102.TANK_ALERT_ALARM | 0 | TANK.TK-102.HIGH_LEVEL | 0 | TK-102 | Primary Radar | TANK.TK-102.HIGH_HIGH_LEVEL | 0 | TK-102 | Primary Radar | LEVELSWITCH.VIB TK102.SWITCH_STATUS | 0 | VIB TK102 | VFT | LEVELSWITCH.VIB TK102.PROOF_TEST_OK | 0 | VIB TK102 | VFT | LEVELSWITCH.VIB TK102.PROOF_TEST_FAILED | 0 | VIB TK102 | VFT | LEVELSWITCH.RDR TK102.SWITCH_STATUS | 0 | RDR TK102 | RADAR | LEVELSWITCH.RDR TK102.PROOF_TEST_OK | 0 | RDR TK102 | RADAR | LEVELSWITCH.RDR TK102.PROOF_TEST_FAILED | 0 | RDR TK102 | RADAR | [8 empty] | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV IL2 | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED RCL | MOV.DBBV-05.OPEN_STATUS | 0 | DBBV-05 | MOV IL2 | MOV.DBBV-07.OPEN_STATUS | 0 | DBBV-07 | MOV IL2 | MOV.DBBV-06.OPEN_STATUS | 0 | DBBV-06 | MOV OL | MOV.DBBV-08.CLOSE_STATUS | 0 | DBBV-08 | MOV OL1
1588 | Vashi | TK-103_BS VI HSD | TK-103 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-103.LEVEL |  | TK-103 | Primary Radar |  |  | TANK.TK-103.TANK_ALERT_ALARM | 0 | TANK.TK-103.HIGH_LEVEL | 0 | TK-103 | Primary Radar | TANK.TK-103.HIGH_HIGH_LEVEL | 0 | TK-103 | Primary Radar | LEVELSWITCH.VIB TK103.SWITCH_STATUS | 0 | VIB TK103 | VFT | LEVELSWITCH.VIB TK103.PROOF_TEST_OK | 0 | VIB TK103 | VFT | LEVELSWITCH.VIB TK103.PROOF_TEST_FAILED | 0 | VIB TK103 | VFT | LEVELSWITCH.RDR TK103.SWITCH_STATUS | 0 | RDR TK103 | RADAR | LEVELSWITCH.RDR TK103.PROOF_TEST_OK | 0 | RDR TK103 | RADAR | LEVELSWITCH.RDR TK103.PROOF_TEST_FAILED | 0 | RDR TK103 | RADAR | [8 empty] | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV IL2 | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV RCL | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED RCL | MOV.DBBV-09.OPEN_STATUS | 0 | DBBV-09 | MOV IL3 | MOV.DBBV-11.OPEN_STATUS | 0 | DBBV-11 | MOV IL2 | MOV.DBBV-10.OPEN_STATUS | 0 | DBBV-10 | MOV OL | MOV.DBBV-12.CLOSE_STATUS | 0 | DBBV-12 | MOV OL1
1588 | Vashi | TK-104_ETHANOL | TK-104 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-104.LEVEL |  | TK-104 | Primary Radar |  |  | TANK.TK-104.TANK_ALERT_ALARM | 0 | TANK.TK-104.HIGH_LEVEL | 0 | TK-104 | Primary Radar | TANK.TK-104.HIGH_HIGH_LEVEL | 0 | TK-104 | Primary Radar | LEVELSWITCH.VIB TK104.SWITCH_STATUS | 0 | VIB TK104 | VFT | LEVELSWITCH.VIB TK104.PROOF_TEST_OK | 0 | VIB TK104 | VFT | LEVELSWITCH.VIB TK104.PROOF_TEST_FAILED | 0 | VIB TK104 | VFT | LEVELSWITCH.RDR TK104.SWITCH_STATUS | 0 | RDR TK104 | RADAR | LEVELSWITCH.RDR TK104.PROOF_TEST_OK | 0 | RDR TK104 | RADAR | LEVELSWITCH.RDR TK104.PROOF_TEST_FAILED | 0 | RDR TK104 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_OPEN | 0 | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-13.OPEN_STATUS | 0 | DBBV-13 | MOV IL4 | MOV.DBBV-15.OPEN_STATUS | 0 | DBBV-15 | MOV IL2 | MOV.DBBV-14.OPEN_STATUS | 0 | DBBV-14 | MOV OL | MOV.DBBV-16.CLOSE_STATUS | 0 | DBBV-16 | MOV OL1
1588 | Vashi | TK-105_LOW RON MS | TK-105 | AG | LOW RON MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-105.LEVEL |  | TK-105 | Primary Radar |  |  | TANK.TK-105.TANK_ALERT_ALARM | 0 | TANK.TK-105.HIGH_LEVEL | 0 | TK-105 | Primary Radar | TANK.TK-105.HIGH_HIGH_LEVEL | 0 | TK-105 | Primary Radar | LEVELSWITCH.VIB TK105.SWITCH_STATUS | 0 | VIB TK105 | VFT | LEVELSWITCH.VIB TK105.PROOF_TEST_OK | 0 | VIB TK105 | VFT | LEVELSWITCH.VIB TK105.PROOF_TEST_FAILED | 0 | VIB TK105 | VFT | LEVELSWITCH.RDR TK105.SWITCH_STATUS | 0 | RDR TK105 | RADAR | LEVELSWITCH.RDR TK105.PROOF_TEST_OK | 0 | RDR TK105 | RADAR | LEVELSWITCH.RDR TK105.PROOF_TEST_FAILED | 0 | RDR TK105 | RADAR | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV IL2 | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED RCL | MOV.DBBV-17.OPEN_STATUS | 0 | DBBV-17 | MOV IL5 | MOV.DBBV-19.OPEN_STATUS | 0 | DBBV-19 | MOV IL2 | MOV.DBBV-18.OPEN_STATUS | 0 | DBBV-18 | MOV OL | MOV.DBBV-20.CLOSE_STATUS | 0 | DBBV-20 | MOV OL1
1588 | Vashi | TK-106_LOW RON MS | TK-106 | AG | LOW RON MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-106.LEVEL |  | TK-106 | Primary Radar |  |  | TANK.TK-106.TANK_ALERT_ALARM | 0 | TANK.TK-106.HIGH_LEVEL | 0 | TK-106 | Primary Radar | TANK.TK-106.HIGH_HIGH_LEVEL | 0 | TK-106 | Primary Radar | LEVELSWITCH.VIB TK106.SWITCH_STATUS | 0 | VIB TK106 | VFT | LEVELSWITCH.VIB TK106.PROOF_TEST_OK | 0 | VIB TK106 | VFT | LEVELSWITCH.VIB TK106.PROOF_TEST_FAILED | 0 | VIB TK106 | VFT | LEVELSWITCH.RDR TK106.SWITCH_STATUS | 0 | RDR TK106 | RADAR | LEVELSWITCH.RDR TK106.PROOF_TEST_OK | 0 | RDR TK106 | RADAR | LEVELSWITCH.RDR TK106.PROOF_TEST_FAILED | 0 | RDR TK106 | RADAR | [8 empty] | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV IL2 | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV RCL | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED RCL | MOV.DBBV-21.OPEN_STATUS | 0 | DBBV-21 | MOV IL6 | MOV.DBBV-23.OPEN_STATUS | 0 | DBBV-23 | MOV IL2 | MOV.DBBV-22.OPEN_STATUS | 0 | DBBV-22 | MOV OL | MOV.DBBV-24.CLOSE_STATUS | 0 | DBBV-24 | MOV OL1
1588 | Vashi | TK-107_BS VI HSD | TK-107 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-107.LEVEL |  | TK-107 | Primary Radar |  |  | TANK.TK-107.TANK_ALERT_ALARM | 0 | TANK.TK-107.HIGH_LEVEL | 0 | TK-107 | Primary Radar | TANK.TK-107.HIGH_HIGH_LEVEL | 0 | TK-107 | Primary Radar | LEVELSWITCH.VIB TK107.SWITCH_STATUS | 0 | VIB TK107 | VFT | LEVELSWITCH.VIB TK107.PROOF_TEST_OK | 0 | VIB TK107 | VFT | LEVELSWITCH.VIB TK107.PROOF_TEST_FAILED | 0 | VIB TK107 | VFT | LEVELSWITCH.RDR TK107.SWITCH_STATUS | 0 | RDR TK107 | RADAR | LEVELSWITCH.RDR TK107.PROOF_TEST_OK | 0 | RDR TK107 | RADAR | LEVELSWITCH.RDR TK107.PROOF_TEST_FAILED | 0 | RDR TK107 | RADAR | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV IL2 | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV RCL | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED RCL | MOV.DBBV-25.OPEN_STATUS | 0 | DBBV-25 | MOV IL7 |  |  |  |  | MOV.DBBV-26.OPEN_STATUS | 0 | DBBV-26 | MOV OL | MOV.DBBV-28.CLOSE_STATUS | 0 | DBBV-28 | MOV OL1 | MOV.DBBV-27.CLOSE_STATUS | 0 | DBBV-27 | MOV RCL
1588 | Vashi | TK-108_BS VI HSD | TK-108 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-108.LEVEL |  | TK-108 | Primary Radar |  |  | TANK.TK-108.TANK_ALERT_ALARM | 0 | TANK.TK-108.HIGH_LEVEL | 0 | TK-108 | Primary Radar | TANK.TK-108.HIGH_HIGH_LEVEL | 0 | TK-108 | Primary Radar | LEVELSWITCH.VIB TK108.SWITCH_STATUS | 0 | VIB TK108 | VFT | LEVELSWITCH.VIB TK108.PROOF_TEST_OK | 0 | VIB TK108 | VFT | LEVELSWITCH.VIB TK108.PROOF_TEST_FAILED | 0 | VIB TK108 | VFT | LEVELSWITCH.RDR TK108.SWITCH_STATUS | 0 | RDR TK108 | RADAR | LEVELSWITCH.RDR TK108.PROOF_TEST_OK | 0 | RDR TK108 | RADAR | LEVELSWITCH.RDR TK108.PROOF_TEST_FAILED | 0 | RDR TK108 | RADAR | [8 empty] | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV IL2 | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV RCL | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED RCL |  |  |  |  | MOV.DBBV-32.OPEN_STATUS | 0 | DBBV-32 | MOV IL2 | [8 empty] | MOV.DBBV-31.CLOSE_STATUS | 0 | DBBV-31 | MOV RCL
1588 | Vashi | TK-109_BS VI HSD | TK-109 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-109.LEVEL |  | TK-109 | Primary Radar |  |  | TANK.TK-109.TANK_ALERT_ALARM | 0 | TANK.TK-109.HIGH_LEVEL | 0 | TK-109 | Primary Radar | TANK.TK-109.HIGH_HIGH_LEVEL | 0 | TK-109 | Primary Radar | LEVELSWITCH.VIB TK109.SWITCH_STATUS | 0 | VIB TK109 | VFT | LEVELSWITCH.VIB TK109.PROOF_TEST_OK | 0 | VIB TK109 | VFT | LEVELSWITCH.VIB TK109.PROOF_TEST_FAILED | 0 | VIB TK109 | VFT | LEVELSWITCH.RDR TK109.SWITCH_STATUS | 0 | RDR TK109 | RADAR | LEVELSWITCH.RDR TK109.PROOF_TEST_OK | 0 | RDR TK109 | RADAR | LEVELSWITCH.RDR TK109.PROOF_TEST_FAILED | 0 | RDR TK109 | RADAR | [8 empty] | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL2 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED RCL | MOV.DBBV-33.OPEN_STATUS | 0 | DBBV-33 | MOV IL9 | MOV.DBBV-36.OPEN_STATUS | 0 | DBBV-36 | MOV IL2 | MOV.DBBV-34.OPEN_STATUS | 0 | DBBV-34 | MOV OL |  |  |  |  | MOV.DBBV-35.CLOSE_STATUS | 0 | DBBV-35 | MOV RCL
1588 | Vashi | TK-110_SKO | TK-110 | AG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-110.LEVEL |  | TK-110 | Primary Radar |  |  | TANK.TK-110.TANK_ALERT_ALARM | 0 | TANK.TK-110.HIGH_LEVEL | 0 | TK-110 | Primary Radar | TANK.TK-110.HIGH_HIGH_LEVEL | 0 | TK-110 | Primary Radar | LEVELSWITCH.VIB TK110.SWITCH_STATUS | 0 | VIB TK110 | VFT | LEVELSWITCH.VIB TK110.PROOF_TEST_OK | 0 | VIB TK110 | VFT | LEVELSWITCH.VIB TK110.PROOF_TEST_FAILED | 0 | VIB TK110 | VFT | LEVELSWITCH.RDR TK110.SWITCH_STATUS | 0 | RDR TK110 | RADAR | LEVELSWITCH.RDR TK110.PROOF_TEST_OK | 0 | RDR TK110 | RADAR | LEVELSWITCH.RDR TK110.PROOF_TEST_FAILED | 0 | RDR TK110 | RADAR | [16 empty] | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV OL | MOV.ROSOV-22.FAILED_TO_OPEN | 0 | ROSOV-22 | ROSOV FAILED OL | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED RCL | MOV.DBBV-37.OPEN_STATUS | 0 | DBBV-37 | MOV IL10 | MOV.DBBV-40.OPEN_STATUS | 0 | DBBV-40 | MOV IL2 | MOV.DBBV-38.OPEN_STATUS | 0 | DBBV-38 | MOV OL |  |  |  |  | MOV.DBBV-39.CLOSE_STATUS | 0 | DBBV-39 | MOV RCL
1588 | Vashi | TK-111_ATF | TK-111 | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-111.LEVEL |  | TK-111 | Primary Radar |  |  | TANK.TK-111.TANK_ALERT_ALARM | 0 | TANK.TK-111.HIGH_LEVEL | 0 | TK-111 | Primary Radar | TANK.TK-111.HIGH_HIGH_LEVEL | 0 | TK-111 | Primary Radar | LEVELSWITCH.VIB TK111.SWITCH_STATUS | 0 | VIB TK111 | VFT | LEVELSWITCH.VIB TK111.PROOF_TEST_OK | 0 | VIB TK111 | VFT | LEVELSWITCH.VIB TK111.PROOF_TEST_FAILED | 0 | VIB TK111 | VFT | LEVELSWITCH.RDR TK111.SWITCH_STATUS | 0 | RDR TK111 | RADAR | LEVELSWITCH.RDR TK111.PROOF_TEST_OK | 0 | RDR TK111 | RADAR | LEVELSWITCH.RDR TK111.PROOF_TEST_FAILED | 0 | RDR TK111 | RADAR | [16 empty] | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-23.FAILED_TO_OPEN | 0 | ROSOV-23 | ROSOV FAILED OL | MOV.ROSOV-34.OPEN_STATUS | 0 | ROSOV-34 | ROSOV RCL | MOV.ROSOV-34.FAILED_TO_CLOSE | 0 | ROSOV-34 | ROSOV FAILED RCL | MOV.DBBV-41.OPEN_STATUS | 0 | DBBV-41 | MOV IL11 | MOV.DBBV-44.OPEN_STATUS | 0 | DBBV-44 | MOV IL2 | MOV.DBBV-42.OPEN_STATUS | 0 | DBBV-42 | MOV OL |  |  |  |  | MOV.DBBV-43.CLOSE_STATUS | 0 | DBBV-43 | MOV RCL
1588 | Vashi | TK-112_ETHANOL | TK-112 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-112.LEVEL |  | TK-112 | Primary Radar |  |  | TANK.TK-112.TANK_ALERT_ALARM | 0 | TANK.TK-112.HIGH_LEVEL | 0 | TK-112 | Primary Radar | TANK.TK-112.HIGH_HIGH_LEVEL | 0 | TK-112 | Primary Radar | LEVELSWITCH.VIB TK112.SWITCH_STATUS | 0 | VIB TK112 | VFT | LEVELSWITCH.VIB TK112.PROOF_TEST_OK | 0 | VIB TK112 | VFT | LEVELSWITCH.VIB TK112.PROOF_TEST_FAILED | 0 | VIB TK112 | VFT | LEVELSWITCH.RDR TK112.SWITCH_STATUS | 0 | RDR TK112 | RADAR | LEVELSWITCH.RDR TK112.PROOF_TEST_OK | 0 | RDR TK112 | RADAR | LEVELSWITCH.RDR TK112.PROOF_TEST_FAILED | 0 | RDR TK112 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | 0 | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV OL | MOV.ROSOV-24.FAILED_TO_OPEN | 0 | ROSOV-24 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-45.OPEN_STATUS | 0 | DBBV-45 | MOV IL12 | MOV.DBBV-48.OPEN_STATUS | 0 | DBBV-48 | MOV IL2 | MOV.DBBV-46.OPEN_STATUS | 0 | DBBV-46 | MOV OL |  |  |  |  | MOV.DBBV-47.CLOSE_STATUS | 0 | DBBV-47 | MOV RCL
1588 | Vashi | TK-113_ETHANOL | TK-113 | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-113.LEVEL |  | TK-113 | Primary Radar |  |  | TANK.TK-113.TANK_ALERT_ALARM | 0 | TANK.TK-113.HIGH_LEVEL | 0 | TK-113 | Primary Radar | TANK.TK-113.HIGH_HIGH_LEVEL | 0 | TK-113 | Primary Radar | LEVELSWITCH.VIB TK113.SWITCH_STATUS | 0 | VIB TK113 | VFT | LEVELSWITCH.VIB TK113.PROOF_TEST_OK | 0 | VIB TK113 | VFT | LEVELSWITCH.VIB TK113.PROOF_TEST_FAILED | 0 | VIB TK113 | VFT | LEVELSWITCH.RDR TK113.SWITCH_STATUS | 0 | RDR TK113 | RADAR | LEVELSWITCH.RDR TK113.PROOF_TEST_OK | 0 | RDR TK113 | RADAR | LEVELSWITCH.RDR TK113.PROOF_TEST_FAILED | 0 | RDR TK113 | RADAR | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV IL1 | MOV.ROSOV-27.FAILED_TO_CLOSE | 0 | ROSOV-27 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-28.OPEN_STATUS | 0 | ROSOV-28 | ROSOV OL | MOV.ROSOV-28.FAILED_TO_OPEN | 0 | ROSOV-28 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-49.OPEN_STATUS | 0 | DBBV-49 | MOV IL13 | MOV.DBBV-52.OPEN_STATUS | 0 | DBBV-52 | MOV IL2 | MOV.DBBV-50.OPEN_STATUS | 0 | DBBV-50 | MOV OL |  |  |  |  | MOV.DBBV-51.CLOSE_STATUS | 0 | DBBV-51 | MOV RCL
1588 | Vashi | TK-114_LOW RON MS | TK-114 | AG | LOW RON MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-114.LEVEL |  | TK-114 | Primary Radar |  |  | TANK.TK-114.TANK_ALERT_ALARM | 0 | TANK.TK-114.HIGH_LEVEL | 0 | TK-114 | Primary Radar | TANK.TK-114.HIGH_HIGH_LEVEL | 0 | TK-114 | Primary Radar | LEVELSWITCH.VIB TK114.SWITCH_STATUS | 0 | VIB TK114 | VFT | LEVELSWITCH.VIB TK114.PROOF_TEST_OK | 0 | VIB TK114 | VFT | LEVELSWITCH.VIB TK114.PROOF_TEST_FAILED | 0 | VIB TK114 | VFT | LEVELSWITCH.RDR TK114.SWITCH_STATUS | 0 | RDR TK114 | RADAR | LEVELSWITCH.RDR TK114.PROOF_TEST_OK | 0 | RDR TK114 | RADAR | LEVELSWITCH.RDR TK114.PROOF_TEST_FAILED | 0 | RDR TK114 | RADAR | [8 empty] | MOV.ROSOV-31.OPEN_STATUS | 0 | ROSOV-31 | ROSOV IL2 | MOV.ROSOV-31.FAILED_TO_CLOSE | 0 | ROSOV-31 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-30.OPEN_STATUS | 0 | ROSOV-30 | ROSOV RCL | MOV.ROSOV-30.FAILED_TO_CLOSE | 0 | ROSOV-30 | ROSOV FAILED RCL | MOV.DBBV-53.OPEN_STATUS | 0 | DBBV-53 | MOV IL14 | MOV.DBBV-56.OPEN_STATUS | 0 | DBBV-56 | MOV IL2 | MOV.DBBV-54.OPEN_STATUS | 0 | DBBV-54 | MOV OL |  |  |  |  | MOV.DBBV-55.CLOSE_STATUS | 0 | DBBV-55 | MOV RCL
1588 | Vashi | TK-115_BS VI HSD | TK-115 | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-115.LEVEL |  | TK-115 | Primary Radar |  |  | TANK.TK-115.TANK_ALERT_ALARM | 0 | TANK.TK-115.HIGH_LEVEL | 0 | TK-115 | Primary Radar | TANK.TK-115.HIGH_HIGH_LEVEL | 0 | TK-115 | Primary Radar | LEVELSWITCH.VIB TK115.SWITCH_STATUS | 0 | VIB TK115 | VFT | LEVELSWITCH.VIB TK115.PROOF_TEST_OK | 0 | VIB TK115 | VFT | LEVELSWITCH.VIB TK115.PROOF_TEST_FAILED | 0 | VIB TK115 | VFT | LEVELSWITCH.RDR TK115.SWITCH_STATUS | 0 | RDR TK115 | RADAR | LEVELSWITCH.RDR TK115.PROOF_TEST_OK | 0 | RDR TK115 | RADAR | LEVELSWITCH.RDR TK115.PROOF_TEST_FAILED | 0 | RDR TK115 | RADAR | [8 empty] | MOV.ROSOV-33.OPEN_STATUS | 0 | ROSOV-33 | ROSOV IL2 | MOV.ROSOV-33.FAILED_TO_CLOSE | 0 | ROSOV-33 | ROSOV FAILED IL2 | [8 empty] | MOV.ROSOV-32.OPEN_STATUS | 0 | ROSOV-32 | ROSOV RCL | MOV.ROSOV-32.FAILED_TO_CLOSE | 0 | ROSOV-32 | ROSOV FAILED RCL | MOV.DBBV-57.OPEN_STATUS | 0 | DBBV-57 | MOV IL15 | MOV.DBBV-60.OPEN_STATUS | 0 | DBBV-60 | MOV IL2 | MOV.DBBV-58.OPEN_STATUS | 0 | DBBV-58 | MOV OL |  |  |  |  | MOV.DBBV-59.CLOSE_STATUS | 0 | DBBV-59 | MOV RCL
1588 | Vashi | TK-124_WATER | TK-124 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-124.LEVEL |  | TK-124 | Primary Radar
1588 | Vashi | TK-125_WATER | TK-125 | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-125.LEVEL |  | TK-125 | Primary Radar
1588 | Vashi | TK-130_ETHANOL | TK-130 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-130.LEVEL |  | TK-130 | Primary Radar
1588 | Vashi | TK-131_ETHANOL | TK-131 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-131.LEVEL |  | TK-131 | Primary Radar
1588 | Vashi | TK-132_LOW RON MS | TK-132 | UG | LOW RON MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-132.LEVEL |  | TK-132 | Primary Radar
1588 | Vashi | TK-133_BS VI HSD | TK-133 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-133.LEVEL |  | TK-133 | Primary Radar
1588 | Vashi | TK-134_SKO | TK-134 | UG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-134.LEVEL |  | TK-134 | Primary Radar
1588 | Vashi | TK-135_BIOHSD | TK-135 | UG | BIOHSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-135.LEVEL |  | TK-135 | Primary Radar
1588 | Vashi | TK-136_ATF | TK-136 | UG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.TK-136.LEVEL |  | TK-136 | Primary Radar

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | MOV MAINTENANCE OL1 | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1588 | Vashi_M | TK-101_ETHANOL | TK-101 | AG | ETHANOL | TANK.TK-101.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK101.MAINTENANCE_STATUS | 0 | VIB TK101 | VFT | LEVELSWITCH.RDR TK101.MAINTENANCE_STATUS | 0 | RDR TK101 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL |  |  |  |  | MOV.DBBV-01.MAINTENANCE_STATUS | 0 | DBBV-01 | MOV IL1 | MOV.DBBV-03.MAINTENANCE_STATUS | 0 | DBBV-03 | MOV IL2 |  |  |  |  | MOV.DBBV-02.MAINTENANCE_STATUS | 0 | DBBV-02 | MOV OL | MOV.DBBV-04.MAINTENANCE_STATUS | 0 | DBBV-04 | MOV OL1
1588 | Vashi_M | TK-102_SLOP | TK-102 | AG | SLOP | TANK.TK-102.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK102.MAINTENANCE_STATUS | 0 | VIB TK102 | VFT | LEVELSWITCH.RDR TK102.MAINTENANCE_STATUS | 0 | RDR TK102 | RADAR |  |  |  |  | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV RCL | MOV.DBBV-05.MAINTENANCE_STATUS | 0 | DBBV-05 | MOV IL1 | MOV.DBBV-07.MAINTENANCE_STATUS | 0 | DBBV-07 | MOV IL2 |  |  |  |  | MOV.DBBV-06.MAINTENANCE_STATUS | 0 | DBBV-06 | MOV OL | MOV.DBBV-08.MAINTENANCE_STATUS | 0 | DBBV-08 | MOV OL1
1588 | Vashi_M | TK-103_BS VI HSD | TK-103 | AG | BS VI HSD | TANK.TK-103.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK103.MAINTENANCE_STATUS | 0 | VIB TK103 | VFT | LEVELSWITCH.RDR TK103.MAINTENANCE_STATUS | 0 | RDR TK103 | RADAR |  |  |  |  | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV RCL | MOV.DBBV-09.MAINTENANCE_STATUS | 0 | DBBV-09 | MOV IL1 | MOV.DBBV-11.MAINTENANCE_STATUS | 0 | DBBV-11 | MOV IL2 |  |  |  |  | MOV.DBBV-10.MAINTENANCE_STATUS | 0 | DBBV-10 | MOV OL | MOV.DBBV-12.MAINTENANCE_STATUS | 0 | DBBV-12 | MOV OL1
1588 | Vashi_M | TK-104_ETHANOL | TK-104 | AG | ETHANOL | TANK.TK-104.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK104.MAINTENANCE_STATUS | 0 | VIB TK104 | VFT | LEVELSWITCH.RDR TK104.MAINTENANCE_STATUS | 0 | RDR TK104 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL |  |  |  |  | MOV.DBBV-13.MAINTENANCE_STATUS | 0 | DBBV-13 | MOV IL1 | MOV.DBBV-15.MAINTENANCE_STATUS | 0 | DBBV-15 | MOV IL2 |  |  |  |  | MOV.DBBV-14.MAINTENANCE_STATUS | 0 | DBBV-14 | MOV OL | MOV.DBBV-16.MAINTENANCE_STATUS | 0 | DBBV-16 | MOV OL1
1588 | Vashi_M | TK-105_LOW RON MS | TK-105 | AG | LOW RON MS | TANK.TK-105.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK105.MAINTENANCE_STATUS | 0 | VIB TK105 | VFT | LEVELSWITCH.RDR TK105.MAINTENANCE_STATUS | 0 | RDR TK105 | RADAR |  |  |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV RCL | MOV.DBBV-17.MAINTENANCE_STATUS | 0 | DBBV-17 | MOV IL1 | MOV.DBBV-19.MAINTENANCE_STATUS | 0 | DBBV-19 | MOV IL2 |  |  |  |  | MOV.DBBV-18.MAINTENANCE_STATUS | 0 | DBBV-18 | MOV OL | MOV.DBBV-20.MAINTENANCE_STATUS | 0 | DBBV-20 | MOV OL1
1588 | Vashi_M | TK-106_LOW RON MS | TK-106 | AG | LOW RON MS | TANK.TK-106.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK106.MAINTENANCE_STATUS | 0 | VIB TK106 | VFT | LEVELSWITCH.RDR TK106.MAINTENANCE_STATUS | 0 | RDR TK106 | RADAR |  |  |  |  | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV RCL | MOV.DBBV-21.MAINTENANCE_STATUS | 0 | DBBV-21 | MOV IL1 | MOV.DBBV-23.MAINTENANCE_STATUS | 0 | DBBV-23 | MOV IL2 |  |  |  |  | MOV.DBBV-22.MAINTENANCE_STATUS | 0 | DBBV-22 | MOV OL | MOV.DBBV-24.MAINTENANCE_STATUS | 0 | DBBV-24 | MOV OL1
1588 | Vashi_M | TK-107_BS VI HSD | TK-107 | AG | BS VI HSD | TANK.TK-107.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK107.MAINTENANCE_STATUS | 0 | VIB TK107 | VFT | LEVELSWITCH.RDR TK107.MAINTENANCE_STATUS | 0 | RDR TK107 | RADAR |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV RCL | MOV.DBBV-25.MAINTENANCE_STATUS | 0 | DBBV-25 | MOV IL1 |  |  |  | MOV IL2 | MOV.DBBV-27.MAINTENANCE_STATUS | 0 | DBBV-27 | MOV RCL | MOV.DBBV-26.MAINTENANCE_STATUS | 0 | DBBV-26 | MOV OL | MOV.DBBV-28.MAINTENANCE_STATUS | 0 | DBBV-28 | MOV OL1
1588 | Vashi_M | TK-108_BS VI HSD | TK-108 | AG | BS VI HSD | TANK.TK-108.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK108.MAINTENANCE_STATUS | 0 | VIB TK108 | VFT | LEVELSWITCH.RDR TK108.MAINTENANCE_STATUS | 0 | RDR TK108 | RADAR |  |  |  |  | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV RCL |  |  |  |  | MOV.DBBV-32.MAINTENANCE_STATUS | 0 | DBBV-32 | MOV IL2 | MOV.DBBV-31.MAINTENANCE_STATUS | 0 | DBBV-31 | MOV RCL
1588 | Vashi_M | TK-109_BS VI HSD | TK-109 | AG | BS VI HSD | TANK.TK-109.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK109.MAINTENANCE_STATUS | 0 | VIB TK109 | VFT | LEVELSWITCH.RDR TK109.MAINTENANCE_STATUS | 0 | RDR TK109 | RADAR |  |  |  |  | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.DBBV-33.MAINTENANCE_STATUS | 0 | DBBV-33 | MOV IL1 | MOV.DBBV-36.MAINTENANCE_STATUS | 0 | DBBV-36 | MOV IL2 | MOV.DBBV-35.MAINTENANCE_STATUS | 0 | DBBV-35 | MOV RCL | MOV.DBBV-34.MAINTENANCE_STATUS | 0 | DBBV-34 | MOV OL
1588 | Vashi_M | TK-110_SKO | TK-110 | AG | SKO | TANK.TK-110.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK110.MAINTENANCE_STATUS | 0 | VIB TK110 | VFT | LEVELSWITCH.RDR TK110.MAINTENANCE_STATUS | 0 | RDR TK110 | RADAR | [8 empty] | MOV.ROSOV-22.MAINTENANCE_STATUS | 0 | ROSOV-22 | ROSOV OL | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.DBBV-37.MAINTENANCE_STATUS | 0 | DBBV-37 | MOV IL1 | MOV.DBBV-40.MAINTENANCE_STATUS | 0 | DBBV-40 | MOV IL2 | MOV.DBBV-39.MAINTENANCE_STATUS | 0 | DBBV-39 | MOV RCL | MOV.DBBV-38.MAINTENANCE_STATUS | 0 | DBBV-38 | MOV OL
1588 | Vashi_M | TK-111_ATF | TK-111 | AG | ATF | TANK.TK-111.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK111.MAINTENANCE_STATUS | 0 | VIB TK111 | VFT | LEVELSWITCH.RDR TK111.MAINTENANCE_STATUS | 0 | RDR TK111 | RADAR | [8 empty] | MOV.ROSOV-23.MAINTENANCE_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-34.MAINTENANCE_STATUS | 0 | ROSOV-34 | ROSOV RCL | MOV.DBBV-41.MAINTENANCE_STATUS | 0 | DBBV-41 | MOV IL1 | MOV.DBBV-44.MAINTENANCE_STATUS | 0 | DBBV-44 | MOV IL2 | MOV.DBBV-43.MAINTENANCE_STATUS | 0 | DBBV-43 | MOV RCL | MOV.DBBV-42.MAINTENANCE_STATUS | 0 | DBBV-42 | MOV OL
1588 | Vashi_M | TK-112_ETHANOL | TK-112 | AG | ETHANOL | TANK.TK-112.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK112.MAINTENANCE_STATUS | 0 | VIB TK112 | VFT | LEVELSWITCH.RDR TK112.MAINTENANCE_STATUS | 0 | RDR TK112 | RADAR | MOV.ROSOV-25.MAINTENANCE_STATUS | 0 | ROSOV-25 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-24.MAINTENANCE_STATUS | 0 | ROSOV-24 | ROSOV OL |  |  |  |  | MOV.DBBV-45.MAINTENANCE_STATUS | 0 | DBBV-45 | MOV IL1 | MOV.DBBV-48.MAINTENANCE_STATUS | 0 | DBBV-48 | MOV IL2 | MOV.DBBV-47.MAINTENANCE_STATUS | 0 | DBBV-47 | MOV RCL | MOV.DBBV-46.MAINTENANCE_STATUS | 0 | DBBV-46 | MOV OL
1588 | Vashi_M | TK-113_ETHANOL | TK-113 | AG | ETHANOL | TANK.TK-113.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK113.MAINTENANCE_STATUS | 0 | VIB TK113 | VFT | LEVELSWITCH.RDR TK113.MAINTENANCE_STATUS | 0 | RDR TK113 | RADAR | MOV.ROSOV-27.MAINTENANCE_STATUS | 0 | ROSOV-27 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-28.MAINTENANCE_STATUS | 0 | ROSOV-28 | ROSOV OL |  |  |  |  | MOV.DBBV-49.MAINTENANCE_STATUS | 0 | DBBV-49 | MOV IL1 | MOV.DBBV-52.MAINTENANCE_STATUS | 0 | DBBV-52 | MOV IL2 | MOV.DBBV-51.MAINTENANCE_STATUS | 0 | DBBV-51 | MOV RCL | MOV.DBBV-50.MAINTENANCE_STATUS | 0 | DBBV-50 | MOV OL
1588 | Vashi_M | TK-114_LOW RON MS | TK-114 | AG | LOW RON MS | TANK.TK-114.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK114.MAINTENANCE_STATUS | 0 | VIB TK114 | VFT | LEVELSWITCH.RDR TK114.MAINTENANCE_STATUS | 0 | RDR TK114 | RADAR |  |  |  |  | MOV.ROSOV-31.MAINTENANCE_STATUS | 0 | ROSOV-31 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-30.MAINTENANCE_STATUS | 0 | ROSOV-30 | ROSOV RCL | MOV.DBBV-53.MAINTENANCE_STATUS | 0 | DBBV-53 | MOV IL1 | MOV.DBBV-56.MAINTENANCE_STATUS | 0 | DBBV-56 | MOV IL2 | MOV.DBBV-55.MAINTENANCE_STATUS | 0 | DBBV-55 | MOV RCL | MOV.DBBV-54.MAINTENANCE_STATUS | 0 | DBBV-54 | MOV OL
1588 | Vashi_M | TK-115_BS VI HSD | TK-115 | AG | BS VI HSD | TANK.TK-115.MAINTENANCE_STATUS | 0 | LEVELSWITCH.VIB TK115.MAINTENANCE_STATUS | 0 | VIB TK115 | VFT | LEVELSWITCH.RDR TK115.MAINTENANCE_STATUS | 0 | RDR TK115 | RADAR |  |  |  |  | MOV.ROSOV-33.MAINTENANCE_STATUS | 0 | ROSOV-33 | ROSOV IL2 |  |  |  |  | MOV.ROSOV-32.MAINTENANCE_STATUS | 0 | ROSOV-32 | ROSOV RCL | MOV.DBBV-57.MAINTENANCE_STATUS | 0 | DBBV-57 | MOV IL1 | MOV.DBBV-60.MAINTENANCE_STATUS | 0 | DBBV-60 | MOV IL2 | MOV.DBBV-59.MAINTENANCE_STATUS | 0 | DBBV-59 | MOV RCL | MOV.DBBV-58.MAINTENANCE_STATUS | 0 | DBBV-58 | MOV OL
1588 | Vashi_M | TK-124_WATER | TK-124 | AG | WATER
1588 | Vashi_M | TK-125_WATER | TK-125 | AG | WATER
1588 | Vashi_M | TK-130_ETHANOL | TK-130 | UG | ETHANOL | TANK.TK-130.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-131_ETHANOL | TK-131 | UG | ETHANOL | TANK.TK-131.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-132_LOW RON MS | TK-132 | UG | LOW RON MS | TANK.TK-132.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-133_BS VI HSD | TK-133 | UG | BS VI HSD | TANK.TK-133.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-134_SKO | TK-134 | UG | SKO | TANK.TK-134.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-135_BIOHSD | TK-135 | UG | BIOHSD | TANK.TK-135.MAINTENANCE_STATUS | 0
1588 | Vashi_M | TK-136_ATF | TK-136 | UG | ATF | TANK.TK-136.MAINTENANCE_STATUS | 0

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1588 | Vashi | ADTV-PMP-01_POWER_DISPATCH | ADTV-PMP-01 | POWER | Truck Loading | DISPATCH | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1588 | Vashi | ADTV-PMP-02_POWER_DISPATCH | ADTV-PMP-02 | POWER | Truck Loading | DISPATCH | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1588 | Vashi | ADTV-PMP-03_TURBO_DISPATCH | ADTV-PMP-03 | TURBO | Truck Loading | DISPATCH | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1588 | Vashi | ADTV-PMP-04_TURBO_DISPATCH | ADTV-PMP-04 | TURBO | Truck Loading | DISPATCH | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-01_BS VI HSD_DISPATCH | PMP-01 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-02_BS VI HSD_DISPATCH | PMP-02 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-03_BS VI HSD_DISPATCH | PMP-03 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-05_BS VI HSD_DISPATCH | PMP-05 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-06_BS VI HSD_DISPATCH | PMP-06 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-07_BS VI HSD_DISPATCH | PMP-07 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-08_BS VI MS_DISPATCH | PMP-08 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-09_BS VI MS_DISPATCH | PMP-09 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-10_BS VI MS_DISPATCH | PMP-10 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-11_BS VI MS_DISPATCH | PMP-11 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-12_BS VI MS_DISPATCH | PMP-12 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-13_SKO_DISPATCH | PMP-13 | SKO | Truck Loading | DISPATCH | PUMP.PMP-13.ON | 0 | PUMP.PMP-13.REMOTE_STATUS | 1 | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-14_SKO_DISPATCH | PMP-14 | SKO | Truck Loading | DISPATCH | PUMP.PMP-14.ON | 0 | PUMP.PMP-14.REMOTE_STATUS | 1 | PUMP.PMP-14.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-15_ETHANOL_DISPATCH | PMP-15 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-15.ON | 0 | PUMP.PMP-15.REMOTE_STATUS | 1 | PUMP.PMP-15.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-16_ETHANOL_DISPATCH | PMP-16 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-16.ON | 0 | PUMP.PMP-16.REMOTE_STATUS | 1 | PUMP.PMP-16.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-17_ETHANOL_DISPATCH | PMP-17 | ETHANOL | Truck Loading | DISPATCH | PUMP.PMP-17.ON | 0 | PUMP.PMP-17.REMOTE_STATUS | 1 | PUMP.PMP-17.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-18_ATF_DISPATCH | PMP-18 | ATF | Truck Loading | DISPATCH | PUMP.PMP-18.ON | 0 | PUMP.PMP-18.REMOTE_STATUS | 1 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-19_ATF_DISPATCH | PMP-19 | ATF | Truck Loading | DISPATCH | PUMP.PMP-19.ON | 0 | PUMP.PMP-19.REMOTE_STATUS | 1 | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-20_ATF_DISPATCH | PMP-20 | ATF | Truck Loading | DISPATCH | PUMP.PMP-20.ON | 0 | PUMP.PMP-20.REMOTE_STATUS | 1 | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-21_ETHANOL_RECEIPT | PMP-21 | ETHANOL | Truck Loading | RECEIPT | PUMP.PMP-21.ON | 0 | PUMP.PMP-21.REMOTE_STATUS | 1 | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-22_ETHANOL_RECEIPT | PMP-22 | ETHANOL | Truck Loading | RECEIPT | PUMP.PMP-22.ON | 0 | PUMP.PMP-22.REMOTE_STATUS | 1 | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-23_ETHANOL_RECEIPT | PMP-23 | ETHANOL | Truck Loading | RECEIPT | PUMP.PMP-23.ON | 0 | PUMP.PMP-23.REMOTE_STATUS | 1 | PUMP.PMP-23.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-24_BS VI HSD_DISPATCH | PMP-24 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-24.ON | 0 | PUMP.PMP-24.REMOTE_STATUS | 1 | PUMP.PMP-24.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-25_BS VI MS_DISPATCH | PMP-25 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-25.ON | 0 | PUMP.PMP-25.REMOTE_STATUS | 1 | PUMP.PMP-25.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-26_SKO_DISPATCH | PMP-26 | SKO | Truck Loading | DISPATCH | PUMP.PMP-26.ON | 0 | PUMP.PMP-26.REMOTE_STATUS | 1 | PUMP.PMP-26.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-27_ETHANOL_RECEIPT | PMP-27 | ETHANOL | Truck Loading | RECEIPT | PUMP.PMP-27.ON | 0 | PUMP.PMP-27.REMOTE_STATUS | 1 | PUMP.PMP-27.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-28_ATF_DISPATCH | PMP-28 | ATF | Truck Loading | DISPATCH | PUMP.PMP-28.ON | 0 | PUMP.PMP-28.REMOTE_STATUS | 1 | PUMP.PMP-28.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-29_BS VI HSD_DISPATCH | PMP-29 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-29.ON | 0 | PUMP.PMP-29.REMOTE_STATUS | 1 | PUMP.PMP-29.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-30_BS VI HSD_DISPATCH | PMP-30 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-30.ON | 0 | PUMP.PMP-30.REMOTE_STATUS | 1 | PUMP.PMP-30.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-31_BS VI MS_DISPATCH | PMP-31 | BS VI MS | Truck Loading | DISPATCH | PUMP.PMP-31.ON | 0 | PUMP.PMP-31.REMOTE_STATUS | 1 | PUMP.PMP-31.MAINTENANCE_STATUS | 0
1588 | Vashi | PMP-32_BS VI HSD_DISPATCH | PMP-32 | BS VI HSD | Truck Loading | DISPATCH | PUMP.PMP-32.ON | 0 | PUMP.PMP-32.REMOTE_STATUS | 1 | PUMP.PMP-32.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction | PUMP ON STATUS | Normal value | PUMP LR STATUS | Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | Normal value | FIRE PUMP FAIL TO START 2 | Normal value | FIRE PUMP FAIL TO START 3 | Normal value | FIRE PUMP FAIL TO START 4 | Normal value | FIRE PUMP FAIL TO START 5 | Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP FAIL TO START STANDBY1 | Normal value | FIRE PUMP FAIL TO START STANDBY2 | Normal value | FIRE PUMP TRIPPED FAULT | Normal value | FIRE PUMP LLOP ALARM | Normal value | FIRE PUMP HWT ALARM | Normal value
1588 | Vashi | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-03.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-04_Water_DISPATCH | FWP-04 | Water | PH | DISPATCH | PUMP.FWP-04.ON | 0 | PUMP.FWP-04.REMOTE_STATUS | 1 | PUMP.FWP-04.MAINTENANCE_STATUS | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-04.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-04.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-04.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-04.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-05_Water_DISPATCH | FWP-05 | Water | PH | DISPATCH | PUMP.FWP-05.ON | 0 | PUMP.FWP-05.REMOTE_STATUS | 1 | PUMP.FWP-05.MAINTENANCE_STATUS | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-05.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-05.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-05.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-05.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-06_Water_DISPATCH | FWP-06 | Water | PH | DISPATCH | PUMP.FWP-06.ON | 0 | PUMP.FWP-06.REMOTE_STATUS | 1 | PUMP.FWP-06.MAINTENANCE_STATUS | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-06.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-06.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-06.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-06.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | FWP-07_Water_DISPATCH | FWP-07 | Water | PH | DISPATCH | PUMP.FWP-07.ON | 0 | PUMP.FWP-07.REMOTE_STATUS | 1 | PUMP.FWP-07.MAINTENANCE_STATUS | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN5 | 0 |  |  | PUMP.FWP-07.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-07.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-07.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-07.HIGH_TEMPERATURE_ALARM | 0
1588 | Vashi | JCY-01_Water_DISPATCH | JCY-01 | Water | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 | [8 empty] | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 |  |  |  |  | PUMP.JCY-01.PUMP_TRIPPED | 0
1588 | Vashi | JCY-02_Water_DISPATCH | JCY-02 | Water | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 | [8 empty] | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 |  |  |  |  | PUMP.JCY-02.PUMP_TRIPPED | 0
1588 | Vashi | Farthest Point PT_WP_DISPATCH | Farthest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1588 | Vashi | Nearest Point PT_WP_DISPATCH | Nearest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | Normal Value | LOW BATTERY | Normal Value | UPS ON | Normal Value | UPS MAIN AC FAIL | Normal Value
1588 | Vashi | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.UPS_ON | 0 | UPS.UPS-01.MAIN_AC_FAIL | 0
1588 | Vashi | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.UPS_ON | 0 | UPS.UPS-02.MAIN_AC_FAIL | 0
1588 | Vashi | UPS-03_Control Room | UPS-03 | Control Room |  |  |  |  | UPS.UPS-03.UPS_ON | 0 | UPS.UPS-03.MAIN_AC_FAIL | 0
1588 | Vashi | UPS-04_Control Room | UPS-04 | Control Room |  |  |  |  | UPS.UPS-04.UPS_ON | 0 | UPS.UPS-04.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC C IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC D IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1588 | Vashi | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLC A | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLC B
1588 | Vashi | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLC B | PLC.SFTPLC.SFTPLCC_IS_MASTER | 1 | SFTPLC | PLC C | PLC.SFTPLC.SFTPLCD_IS_MASTER | 1 | SFTPLC | PLC D | PLC.SFTPLC.PLCA_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLC B

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | Normal Value | HCD 20 % ALARM | Normal Value | HCD FAULT | Normal Value | MISALIGNMENT FAULT | Normal Value | HCD MAINTENANCE | Normal Value | HCD Hooter Activated | Normal value
1588 | Vashi | HDS_01_OPEN PATH_OLD PUMP HOUSE | HDS_01 | OPEN PATH | OLD PUMP HOUSE | GDS.HDS_01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_02_OPEN PATH_OMC MANIFOLD AREA | HDS_02 | OPEN PATH | OMC MANIFOLD AREA | GDS.HDS_02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_03_OPEN PATH_TANK-101/113-OPENPATH | HDS_03 | OPEN PATH | TANK-101/113-OPENPATH | GDS.HDS_03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_04_OPEN PATH_TANK-105/114-OPENPATH | HDS_04 | OPEN PATH | TANK-105/114-OPENPATH | GDS.HDS_04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_05_POINT TYPE_TANK-106-POINT TYPE | HDS_05 | POINT TYPE | TANK-106-POINT TYPE | GDS.HDS_05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_06_POINT TYPE_OLD PUMP HOUSE | HDS_06 | POINT TYPE | OLD PUMP HOUSE | GDS.HDS_06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_07_POINT TYPE_TK-103 POINT TYPE | HDS_07 | POINT TYPE | TK-103 POINT TYPE | GDS.HDS_07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_22_OPEN PATH_OLD PUMP HOUSE | HDS_22 | OPEN PATH | OLD PUMP HOUSE | GDS.HDS_22.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_22.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_22.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_22.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_22.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_23_OPEN PATH_TK-101/104-OPEN PATH | HDS_23 | OPEN PATH | TK-101/104-OPEN PATH | GDS.HDS_23.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_23.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_23.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_23.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_23.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_24_OPEN PATH_NEW PH1-OPENPATH | HDS_24 | OPEN PATH | NEW PH1-OPENPATH | GDS.HDS_24.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_24.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_24.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_24.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_24.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_25_OPEN PATH_NEW PH2-OPENPATH | HDS_25 | OPEN PATH | NEW PH2-OPENPATH | GDS.HDS_25.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_25.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_25.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_25.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_25.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_26_POINT TYPE_NEW PH2-POINT-TYPE-1 | HDS_26 | POINT TYPE | NEW PH2-POINT-TYPE-1 | GDS.HDS_26.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_26.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_26.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_26.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_26.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_27_POINT TYPE_NEW PH2-POINT-TYPE-2 | HDS_27 | POINT TYPE | NEW PH2-POINT-TYPE-2 | GDS.HDS_27.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_27.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_27.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_27.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_27.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1588 | Vashi | HDS_28_POINT TYPE_ETP AREA-POINT-TYPE | HDS_28 | POINT TYPE | ETP AREA-POINT-TYPE | GDS.HDS_28.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS_28.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS_28.CRITICAL_FAULT_ALARM | 0 | GDS.HDS_28.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS_28.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1588 | Vashi | DYKE-01 | DRAINVALVE.DYKE-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1588 | Vashi | DYKE-02 | DRAINVALVE.DYKE-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1588 | Vashi | DYKE-03 | DRAINVALVE.DYKE-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1588 | Vashi | DYKE-04 | DRAINVALVE.DYKE-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1588 | Vashi | DYKE-05 | DRAINVALVE.DYKE-05.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | Normal value | BARRIER GATE LR STATUS | Normal value
1588 | Vashi | EntryGate1 | GATE.EntryGate1.OPEN_STATUS | 1 | GATE.EntryGate1.REMOTE_STATUS | 1
1588 | Vashi | ExitGate1 | GATE.ExitGate1.OPEN_STATUS | 1 | GATE.ExitGate1.REMOTE_STATUS | 1
1588 | Vashi | EntryGate2 | GATE.EntryGate2.OPEN_STATUS | 1 | GATE.EntryGate2.REMOTE_STATUS | 1
1588 | Vashi | ExitGate2 | GATE.ExitGate2.OPEN_STATUS | 1 | GATE.ExitGate2.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | Normal Value
1588 | Vashi | HTR1_HOOTER_FIELD_1 | HTR1 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1588 | Vashi | HTR2_HOOTER_FIELD_2 | HTR2 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1588 | Vashi | HTR3_HOOTER_FIELD_3 | HTR3 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1588 | Vashi | HTR4_HOOTER_FIELD_4 | HTR4 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1588 | Vashi | HTR5_HOOTER_FIELD_5 | HTR5 | HOOTER_FIELD_5 | PLC.SFTPLC.HOOTER_FIELD_5 | 0
1588 | Vashi | HTR6_HOOTER_FIELD_6 | HTR6 | HOOTER_FIELD_6 | PLC.SFTPLC.HOOTER_FIELD_6 | 0
1588 | Vashi | HTR7_HOOTER_FOR_SECURITY_ROOM | HTR7 | HOOTER_FOR_SECURITY_ROOM | PLC.SFTPLC.HOOTER_FOR_SECURITY_ROOM | 0
1588 | Vashi | HTR8_HOOTER_RESET_STATUS | HTR8 | HOOTER_RESET_STATUS | PLC.SFTPLC.HOOTER_RESET_STATUS | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | Normal Value | ESD MAINTENANCE STATUS | Normal Value | All ROSOVs closed | Normal Value | Barrier Gate opened | Normal Value | TLF Gantry Permissive Power Off | Normal Value | All TLF Product Pumps Stopped | Normal Value | All Tanks in Dormant Mode | Normal Value | All DBBVs Closed | Normal Value | ESD Command To Process PLC | Normal Value | Siren Activated | Normal Value | ESD Hooter activated in control room | Normal Value | Power ESD Activation after 120 Sec | Normal Value | TTL Dispatch in Dormant Mode | Normal Value
1588 | Vashi | ESD-18_456 | ESD-18 | ESD-36 | 456 | ESD.ESD-18.ESD_STATUS | 0 | ESD.ESD-18.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-19_CONTROL ROOM | ESD-19 | ESD-17 | CONTROL ROOM | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-20_TLF-1 WALKWAY | ESD-20 | ESD-18 | TLF-1 WALKWAY | ESD.ESD-20.ESD_STATUS | 0 | ESD.ESD-20.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-21_TLF-1 BAY 05 | ESD-21 | ESD-19 | TLF-1 BAY 05 | ESD.ESD-21.ESD_STATUS | 0 | ESD.ESD-21.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-22_TLF-2 BAY 12 | ESD-22 | ESD-21 | TLF-2 BAY 12 | ESD.ESD-22.ESD_STATUS | 0 | ESD.ESD-22.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-23_TLF-2 WALKWAY | ESD-23 | ESD-20 | TLF-2 WALKWAY | ESD.ESD-23.ESD_STATUS | 0 | ESD.ESD-23.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-24_NEW PUMP HOUSE 2 | ESD-24 | ESD-24 | NEW PUMP HOUSE 2 | ESD.ESD-24.ESD_STATUS | 0 | ESD.ESD-24.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-25_NEW PUMP HOUSE 1 | ESD-25 | ESD-25 | NEW PUMP HOUSE 1 | ESD.ESD-25.ESD_STATUS | 0 | ESD.ESD-25.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-26_NEW UG TANK FARM | ESD-26 | ESD-26 | NEW UG TANK FARM | ESD.ESD-26.ESD_STATUS | 0 | ESD.ESD-26.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-27_TLF-3 WALKWAY | ESD-27 | ESD-22 | TLF-3 WALKWAY | ESD.ESD-27.ESD_STATUS | 0 | ESD.ESD-27.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-28_TLF-3 BAY 18 | ESD-28 | ESD-23 | TLF-3 BAY 18 | ESD.ESD-28.ESD_STATUS | 0 | ESD.ESD-28.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-401_OLD PUMP HOUSE | ESD-401 | ESD-09 | OLD PUMP HOUSE | ESD.ESD-401.ESD_STATUS | 0 | ESD.ESD-401.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-404_TT OUT GATE | ESD-404 | ESD-02 | TT OUT GATE | ESD.ESD-404.ESD_STATUS | 0 | ESD.ESD-404.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-405_QC LAB | ESD-405 | ESD-03 | QC LAB | ESD.ESD-405.ESD_STATUS | 0 | ESD.ESD-405.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-406_NEAR MPSPL PATHWAY | ESD-406 | ESD-06 | NEAR MPSPL PATHWAY | ESD.ESD-406.ESD_STATUS | 0 | ESD.ESD-406.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-407_NEAR OLD MCC | ESD-407 | ESD-08 | NEAR OLD MCC | ESD.ESD-407.ESD_STATUS | 0 | ESD.ESD-407.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-408_MPSPL PUMP HOUSE | ESD-408 | ESD-07 | MPSPL PUMP HOUSE | ESD.ESD-408.ESD_STATUS | 0 | ESD.ESD-408.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-410_NEAR TK-108 | ESD-410 | ESD-15 | NEAR TK-108 | ESD.ESD-410.ESD_STATUS | 0 | ESD.ESD-410.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-411_NEAR TK-113 | ESD-411 | ESD-10 | NEAR TK-113 | ESD.ESD-411.ESD_STATUS | 0 | ESD.ESD-411.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-412_NEAR TK-103 | ESD-412 | ESD-14 | NEAR TK-103 | ESD.ESD-412.ESD_STATUS | 0 | ESD.ESD-412.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-413_NEAR TK-101 | ESD-413 | ESD-11 | NEAR TK-101 | ESD.ESD-413.ESD_STATUS | 0 | ESD.ESD-413.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-414_NEAR TK-115 | ESD-414 | ESD-13 | NEAR TK-115 | ESD.ESD-414.ESD_STATUS | 0 | ESD.ESD-414.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-415_NEAR SCRAP YARD | ESD-415 | ESD-12 | NEAR SCRAP YARD | ESD.ESD-415.ESD_STATUS | 0 | ESD.ESD-415.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-417_TT IN GATE | ESD-417 | ESD-01 | TT IN GATE | ESD.ESD-417.ESD_STATUS | 0 | ESD.ESD-417.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-501_ADMIN BUILDING | ESD-501 | ESD-04 | ADMIN BUILDING | ESD.ESD-501.ESD_STATUS | 0 | ESD.ESD-501.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-502_VISITOR ENTRY GATE | ESD-502 | ESD-05 | VISITOR ENTRY GATE | ESD.ESD-502.ESD_STATUS | 0 | ESD.ESD-502.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-503_LIC ROOM | ESD-503 | ESD-16 | LIC ROOM | ESD.ESD-503.ESD_STATUS | 0 | ESD.ESD-503.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-CENTRAL_CENTRAL ESD | ESD-CENTRAL | ESD-CENTRAL | CENTRAL ESD | ESD.ESD-CENTRAL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-PIPELINE_PIPELINE ESD | ESD-PIPELINE | ESD-PIPELINE | PIPELINE ESD | ESD.ESD-PIPELINE.ESD_STATUS | 0 | ESD.ESD-PIPELINE.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0
1588 | Vashi | ESD-SOFT_SOFT ESD | ESD-SOFT | ESD-SOFT | SOFT ESD | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1588 | Vashi | LP 01_BC-01A_ATF | LP 01 | TLF | BC-01A | ATF | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 02_BC-01B_ATF | LP 02 | TLF | BC-01B | ATF | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 03_BC-02A_SKO | LP 03 | TLF | BC-02A | SKO | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 04_BC-02B_SKO | LP 04 | TLF | BC-02B | SKO | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 05_BC-03A_LOW RON MS | LP 05 | TLF | BC-03A | LOW RON MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 07_BC-04A_BS VI HSD | LP 07 | TLF | BC-04A | BS VI HSD | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 09_BC-05A_LOW RON MS | LP 09 | TLF | BC-05A | LOW RON MS | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 11_BC-06A_LOW RON MS | LP 11 | TLF | BC-06A | LOW RON MS | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 13_BC-07A_LOW RON MS | LP 13 | TLF | BC-07A | LOW RON MS | SmartLoad-Dual.BC-07A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 14_BC-07B_BS VI HSD | LP 14 | TLF | BC-07B | BS VI HSD | SmartLoad-Dual.BC-07B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-07B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 15_BC-08A_LOW RON MS | LP 15 | TLF | BC-08A | LOW RON MS | SmartLoad-Dual.BC-08A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-08A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-08A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-08A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-08A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 16_BC-08B_BS VI HSD | LP 16 | TLF | BC-08B | BS VI HSD | SmartLoad-Dual.BC-08B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-08B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-08B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-08B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-08B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-08B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-08B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 17_BC-09A_LOW RON MS | LP 17 | TLF | BC-09A | LOW RON MS | SmartLoad-Dual.BC-09A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 18_BC-09B_BS VI HSD | LP 18 | TLF | BC-09B | BS VI HSD | SmartLoad-Dual.BC-09B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-09B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 19_BC-10A_LOW RON MS | LP 19 | TLF | BC-10A | LOW RON MS | SmartLoad-Dual.BC-10A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 20_BC-10B_BS VI HSD | LP 20 | TLF | BC-10B | BS VI HSD | SmartLoad-Dual.BC-10B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-10B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-10B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 21_BC-11A_LOW RON MS | LP 21 | TLF | BC-11A | LOW RON MS | SmartLoad-Dual.BC-11A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-11A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-11A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-11A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-11A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 22_BC-11B_BS VI HSD | LP 22 | TLF | BC-11B | BS VI HSD | SmartLoad-Dual.BC-11B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-11B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-11B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 23_BC-12A_LOW RON MS | LP 23 | TLF | BC-12A | LOW RON MS | SmartLoad-Dual.BC-12A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-12A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-12A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-12A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-12A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 24_BC-12B_BS VI HSD | LP 24 | TLF | BC-12B | BS VI HSD | SmartLoad-Dual.BC-12B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-12B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-12B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 25_BC-13A_LOW RON MS | LP 25 | TLF | BC-13A | LOW RON MS | SmartLoad-Dual.BC-13A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 26_BC-13B_BS VI HSD | LP 26 | TLF | BC-13B | BS VI HSD | SmartLoad-Dual.BC-13B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-13B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-13B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 27_BC-14A_LOW RON MS | LP 27 | TLF | BC-14A | LOW RON MS | SmartLoad-Dual.BC-14A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 28_BC-14B_BS VI HSD | LP 28 | TLF | BC-14B | BS VI HSD | SmartLoad-Dual.BC-14B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-14B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-14B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 29_BC-15A_LOW RON MS | LP 29 | TLF | BC-15A | LOW RON MS | SmartLoad-Dual.BC-15A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 30_BC-15B_BS VI HSD | LP 30 | TLF | BC-15B | BS VI HSD | SmartLoad-Dual.BC-15B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-15B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-15B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 31_BC-16A_BS VI HSD | LP 31 | TLF | BC-16A | BS VI HSD | SmartLoad-Dual.BC-16A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-16A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-16A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-16A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 32_BC-16B_BS VI HSD | LP 32 | TLF | BC-16B | BS VI HSD | SmartLoad-Dual.BC-16B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-16B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-16B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-16B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-16B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-16B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-16B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 33_BC-17A_LOW RON MS | LP 33 | TLF | BC-17A | LOW RON MS | SmartLoad-Dual.BC-17A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-17A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-17A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-17A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-17A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-17A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-17A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-17A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-17A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-17A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 34_BC-17B_BS VI HSD | LP 34 | TLF | BC-17B | BS VI HSD | SmartLoad-Dual.BC-17B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-17B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-17B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-17B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-17B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-17B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-17B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-17B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 35_BC-18A_LOW RON MS | LP 35 | TLF | BC-18A | LOW RON MS | SmartLoad-Dual.BC-18A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-18A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-18A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-18A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-18A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-18A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-18A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-18A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-18A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-18A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 36_BC-18B_BS VI HSD | LP 36 | TLF | BC-18B | BS VI HSD | SmartLoad-Dual.BC-18B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-18B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-18B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-18B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-18B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-18B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-18B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-18B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 37_BC-19A_LOW RON MS | LP 37 | TLF | BC-19A | LOW RON MS | SmartLoad-Dual.BC-19A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-19A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-19A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-19A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-19A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-19A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-19A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-19A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-19A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-19A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 38_BC-19B_BS VI HSD | LP 38 | TLF | BC-19B | BS VI HSD | SmartLoad-Dual.BC-19B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-19B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-19B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-19B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-19B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-19B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-19B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-19B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 39_BC-20A_LOW RON MS | LP 39 | TLF | BC-20A | LOW RON MS | SmartLoad-Dual.BC-20A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-20A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-20A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-20A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-20A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-20A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-20A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-20A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-20A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-20A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1588 | Vashi | LP 40_BC-20B_BS VI HSD | LP 40 | TLF | BC-20B | BS VI HSD | SmartLoad-Dual.BC-20B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-20B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-20B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-20B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-20B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-20B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-20B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-20B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1588 | Vashi | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1588 | Vashi | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1588 | Vashi | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1588 | Vashi | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1588 | Vashi | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1588 | Vashi | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1588 | Vashi | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1588 | Vashi | LRC Switch Over | CLIENT.LRCVASHI1.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Fire Engine4 | Normal Value | Fire Engine5 | Normal Value | Fire Engine6 | Normal Value | Fire Engine7 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1588 | Vashi | Operability Index | PUMP.FWP-01.ON | 1 | PUMP.FWP-02.ON | 1 | PUMP.FWP-03.ON | 1 | PUMP.FWP-04.ON | 1 | PUMP.FWP-05.ON | 1 | PUMP.FWP-06.ON | 1 | PUMP.FWP-07.ON | 1 | PUMP.JCY-01.ON | 1 | PUMP.JCY-02.ON | 1 | PressureTransmitter.PT-01.PRESSURE |  | PressureTransmitter.PT-02.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL |  | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1