## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH HIGH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1892 | Kozikode | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL | [8 empty] | MOV.MOV-01.OPEN_STATUS | 0 | MOV-01 | MOV IL1 |  |  |  |  | MOV.MOV-02.OPEN_STATUS | 0 | MOV-02 | MOV OL
1892 | Kozikode | TK-02_BS VI MS | TK-02 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | [8 empty] | MOV.MOV-03.OPEN_STATUS | 0 | MOV-03 | MOV IL2 |  |  |  |  | MOV.MOV-04.OPEN_STATUS | 0 | MOV-04 | MOV OL
1892 | Kozikode | TK-03_ETHANOL | TK-03 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | [56 empty] | MOV.MOV-05.OPEN_STATUS | 0 | MOV-05 | MOV IL3
1892 | Kozikode | TK-04_ETHANOL | TK-04 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | [56 empty] | MOV.MOV-06.OPEN_STATUS | 0 | MOV-06 | MOV IL4
1892 | Kozikode | TK-05_BS VI MS | TK-05 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | [56 empty] | MOV.MOV-07.OPEN_STATUS | 0 | MOV-07 | MOV IL5
1892 | Kozikode | TK-06_BS VI MS | TK-06 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar | [56 empty] | MOV.MOV-08.OPEN_STATUS | 0 | MOV-08 | MOV IL6
1892 | Kozikode | TK-07_BIO DIESEL | TK-07 | UG | BIO DIESEL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar | [56 empty] | MOV.MOV-09.OPEN_STATUS | 0 | MOV-09 | MOV IL7
1892 | Kozikode | TK-08_BS VI HSD | TK-08 | UG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar | [56 empty] | MOV.MOV-10.OPEN_STATUS | 0 | MOV-10 | MOV IL8
1892 | Kozikode | TK-09_BS VI MS | TK-09 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar | [56 empty] | MOV.MOV-11.OPEN_STATUS | 0 | MOV-11 | MOV IL9
1892 | Kozikode | WTK-01_WATER | WTK-01 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.WTK-01.LEVEL |  | WTK-0 | Primary Radar
1892 | Kozikode | WTK-02_WATER | WTK-02 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.WTK-02.LEVEL |  | WTK-0 | Primary Radar

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1892 | Kozikode_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV OL |  |  |  |  | MOV.MOV-01.MAINTENANCE_STATUS | 0 | MOV-01 | MOV IL1 | [8 empty] | MOV.MOV-02.MAINTENANCE_STATUS | 0 | MOV-02 | MOV OL
1892 | Kozikode_M | TK-02_BS VI MS | TK-02 | AG | BS VI MS | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL |  |  |  |  | MOV.MOV-03.MAINTENANCE_STATUS | 0 | MOV-03 | MOV IL2 | [8 empty] | MOV.MOV-04.MAINTENANCE_STATUS | 0 | MOV-04 | MOV OL
1892 | Kozikode_M | TK-03_ETHANOL | TK-03 | UG | ETHANOL | TANK.TK-03.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-05.MAINTENANCE_STATUS | 0 | MOV-05 | MOV IL3
1892 | Kozikode_M | TK-04_ETHANOL | TK-04 | UG | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-06.MAINTENANCE_STATUS | 0 | MOV-06 | MOV IL4
1892 | Kozikode_M | TK-05_BS VI MS | TK-05 | UG | BS VI MS | TANK.TK-05.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-07.MAINTENANCE_STATUS | 0 | MOV-07 | MOV IL5
1892 | Kozikode_M | TK-06_BS VI MS | TK-06 | UG | BS VI MS | TANK.TK-06.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-08.MAINTENANCE_STATUS | 0 | MOV-08 | MOV IL6
1892 | Kozikode_M | TK-07_BIO DIESEL | TK-07 | UG | BIO DIESEL | TANK.TK-07.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-09.MAINTENANCE_STATUS | 0 | MOV-09 | MOV IL7
1892 | Kozikode_M | TK-08_BS VI HSD | TK-08 | UG | BS VI HSD | TANK.TK-08.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-10.MAINTENANCE_STATUS | 0 | MOV-10 | MOV IL8
1892 | Kozikode_M | TK-09_BS VI MS | TK-09 | UG | BS VI MS | TANK.TK-09.MAINTENANCE_STATUS | 0 | [24 empty] | MOV.MOV-11.MAINTENANCE_STATUS | 0 | MOV-11 | MOV IL9

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1892 | Kozikode | ADTV-PMP-01_TURBOHSD_Truck Loading | ADTV-PMP-01 | TURBOHSD | TLF | Truck Loading | PUMP.ADTV-PMP-01.ON | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1892 | Kozikode | ADTV-PMP-02_TURBOHSD_Truck Loading | ADTV-PMP-02 | TURBOHSD | TLF | Truck Loading | PUMP.ADTV-PMP-02.ON | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1892 | Kozikode | ADTV-PMP-03_POWERMS_Truck Loading | ADTV-PMP-03 | POWERMS | TLF | Truck Loading | PUMP.ADTV-PMP-03.ON | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1892 | Kozikode | ADTV-PMP-04_POWERMS_Truck Loading | ADTV-PMP-04 | POWERMS | TLF | Truck Loading | PUMP.ADTV-PMP-04.ON | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 1 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-01_BS VI MS_Truck Loading | PMP-01 | BS VI MS | TLF | Truck Loading | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-02_BS VI MS_Truck Loading | PMP-02 | BS VI MS | TLF | Truck Loading | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-03_BS VI HSD_Truck Loading | PMP-03 | BS VI HSD | TLF | Truck Loading | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-04_BS VI HSD_Truck Loading | PMP-04 | BS VI HSD | TLF | Truck Loading | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-05_BS VI MS_Truck Loading | PMP-05 | BS VI MS | TLF | Truck Loading | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-06_BS VI MS_Truck Loading | PMP-06 | BS VI MS | TLF | Truck Loading | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-07_BS VI HSD_Truck Loading | PMP-07 | BS VI HSD | TLF | Truck Loading | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-08_BS VI MS_Truck Loading | PMP-08 | BS VI MS | TLF | Truck Loading | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-09_ETHANOL_Truck Loading | PMP-09 | ETHANOL | TLF | Truck Loading | PUMP.PMP-09.ON | 0 | PUMP.PMP-09.REMOTE_STATUS | 1 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-10_ETHANOL_Truck Loading | PMP-10 | ETHANOL | TLF | Truck Loading | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1892 | Kozikode | PMP-11_BIO DIESEL_Truck Loading | PMP-11 | BIO DIESEL | TLF | Truck Loading | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1892 | Kozikode | TWD-01_BS VI MS_Wagon Loading | TWD-01 | BS VI MS | TWD | Wagon Loading | PUMP.TWD-01.ON | 0 | PUMP.TWD-01.REMOTE_STATUS | 1 | PUMP.TWD-01.MAINTENANCE_STATUS | 0
1892 | Kozikode | TWD-02_BS VI MS_Wagon Loading | TWD-02 | BS VI MS | TWD | Wagon Loading | PUMP.TWD-02.ON | 0 | PUMP.TWD-02.REMOTE_STATUS | 1 | PUMP.TWD-02.MAINTENANCE_STATUS | 0
1892 | Kozikode | TWD-03_BS VI HSD_Wagon Loading | TWD-03 | BS VI HSD | TWD | Wagon Loading | PUMP.TWD-03.ON | 0 | PUMP.TWD-03.REMOTE_STATUS | 1 | PUMP.TWD-03.MAINTENANCE_STATUS | 0
1892 | Kozikode | TWD-04_BS VI HSD_Wagon Loading | TWD-04 | BS VI HSD | TWD | Wagon Loading | PUMP.TWD-04.ON | 0 | PUMP.TWD-04.REMOTE_STATUS | 1 | PUMP.TWD-04.MAINTENANCE_STATUS | 0
1892 | Kozikode | TWD-05_BS VI HSD_Wagon Loading | TWD-05 | BS VI HSD | TWD | Wagon Loading | PUMP.TWD-05.ON | 0 | PUMP.TWD-05.REMOTE_STATUS | 1 | PUMP.TWD-05.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction | PUMP ON STATUS | Normal value | PUMP LR STATUS | Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | Normal value | FIRE PUMP FAIL TO START 2 | Normal value | FIRE PUMP FAIL TO START 3 | Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP TRIPPED FAULT | Normal value | FIRE PUMP LLOP ALARM | Normal value | FIRE PUMP HWT ALARM | Normal value
1892 | Kozikode | FWP-01_Water_DISPATCH | FWP-01 | Water | PH | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1892 | Kozikode | FWP-02_Water_DISPATCH | FWP-02 | Water | PH | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1892 | Kozikode | FWP-03_Water_DISPATCH | FWP-03 | Water | PH | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1892 | Kozikode | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PH | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0
1892 | Kozikode | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PH | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0
1892 | Kozikode | Farthest Point PT_WP_DISPATCH | Farthest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1892 | Kozikode | Nearest Point PT_WP_DISPATCH | Nearest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | Normal Value | LOW BATTERY | Normal Value | UPS ON | Normal Value | UPS MAIN AC FAIL | Normal Value
1892 | Kozikode | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 |  |  | UPS.UPS-01.MAIN_AC_FAIL | 0
1892 | Kozikode | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 |  |  | UPS.UPS-02.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1892 | Kozikode | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1892 | Kozikode | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB | PLC.SFTPLC.PLCAB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLCAB |  |  |  |  | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | Normal Value | HCD 20 % ALARM | Normal Value | HCD FAULT | Normal Value | MISALIGNMENT FAULT | Normal Value | HCD MAINTENANCE | Normal Value | HCD Hooter Activated | Normal value
1892 | Kozikode | GDS-01_PointType_BIO/HSD/MS UG TANK FARM | GDS-01 | PointType | BIO/HSD/MS UG TANK FARM | GDS.GDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.GDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.GDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.GDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.GDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | GDS-02_PointType_MS UG TANK FARM | GDS-02 | PointType | MS UG TANK FARM | GDS.GDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.GDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.GDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.GDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.GDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | GDS-03_PointType_ETH UG TANK FARM | GDS-03 | PointType | ETH UG TANK FARM | GDS.GDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.GDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.GDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.GDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.GDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | GDS-04_PointType_COMPOUND WALL DRAIN PIT | GDS-04 | PointType | COMPOUND WALL DRAIN PIT | GDS.GDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.GDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.GDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.GDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.GDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | HDS-01_OpenPath_Product Pump House | HDS-01 | OpenPath | Product Pump House | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | HDS-02_OpenPath_Near Manifold TK-2 | HDS-02 | OpenPath | Near Manifold TK-2 | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | HDS-03_PointType_TF Near Dyke Valve | HDS-03 | PointType | TF Near Dyke Valve | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | HDS-04_PointType_PIPE MANIFOLD | HDS-04 | PointType | PIPE MANIFOLD | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | HDS-05_PointType_Pipe Manifold | HDS-05 | PointType | Pipe Manifold | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1892 | Kozikode | DYKE-01 | DRAINVALVE.DYKE-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | DYKE-02 | DRAINVALVE.DYKE-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1892 | Kozikode | DYKE-03 | DRAINVALVE.DYKE-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | Normal value | BARRIER GATE LR STATUS | Normal value
1892 | Kozikode | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1892 | Kozikode | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | Normal Value
1892 | Kozikode | HOOTER_HOOTER_FIELD_2 | HOOTER | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1892 | Kozikode | HOOTER_HOOTER_FIELD_4 | HOOTER | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1892 | Kozikode | HOOTER_HOOTER_FOR_RIMSEAL_CR | HOOTER | HOOTER_FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | Normal Value | ESD MAINTENANCE STATUS | Normal Value | All ROSOVs closed | Normal Value | Barrier Gate opened | Normal Value | TLF Gantry Permissive Power Off | Normal Value | All TLF Product Pumps Stopped | Normal Value | All Tanks in Dormant Mode | Normal Value | All DBBVs Closed | Normal Value | ESD Command To Process PLC | Normal Value | Siren Activated | Normal Value | ESD Hooter activated in control room | Normal Value | Power ESD Activation after 120 Sec | Normal Value | TTL Dispatch in Dormant Mode | Normal Value
1892 | Kozikode | ESD-01_LOCATION INCHARGE ROOM | ESD-01 | ESD-01(ESD-PB-04) | LOCATION INCHARGE ROOM | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-02_SECURITY ROOM | ESD-02 | ESD-03(ESD-PB-07) | SECURITY ROOM | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-03_TANK FARM 1 DYKE VALVE | ESD-03 | ESD-09(ESD-PB-14) | TANK FARM 1 DYKE VALVE | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-04_WAGON SIDING NORTH SIDE | ESD-04 | ESD-13(ESD-PB-02) | WAGON SIDING NORTH SIDE | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-05_CONTROL ROOM | ESD-05 | ESD-02(ESD-PB-05) | CONTROL ROOM | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-07_TT GANTRY NEAR BAY 5 | ESD-07 | ESD-06(ESD-PB-20) | TT GANTRY NEAR BAY 5 | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-08_TANK FARM 2 WEST SIDE | ESD-08 | ESD-10(ESD-PB-09) | TANK FARM 2 WEST SIDE | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-09_TANK FARM 3 EAST SIDE | ESD-09 | ESD-11(ESD-PB-18) | TANK FARM 3 EAST SIDE | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-10_PMCC ROOM | ESD-10 | ESD-04(ESD-PB-16) | PMCC ROOM | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-11_TT GANTRY WALKWAY | ESD-11 | ESD-07(ESD-PB-12) | TT GANTRY WALKWAY | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-12_TT PARKING AREA | ESD-12 | ESD-05(ESD-PB-13) | TT PARKING AREA | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-13_PRODUCT PUMP HOUSE | ESD-13 | ESD-12(ESD-PB-15) | PRODUCT PUMP HOUSE | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-14_CENTRAL ESD | ESD-14 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-14.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-18_WAGON SIDING CENTER WEST | ESD-18 | ESD-15(ESD-PB-10) | WAGON SIDING CENTER WEST | ESD.ESD-18.ESD_STATUS | 0 | ESD.ESD-18.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD-19_WAGON SIDING CENTER EAST | ESD-19 | ESD-14(ESD-PB-19) | WAGON SIDING CENTER EAST | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD_17_BEHIND TT GANTRY | ESD_17 | ESD-08(ESD-PB-11) | BEHIND TT GANTRY | ESD.ESD_17.ESD_STATUS | 0 | ESD.ESD_17.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0
1892 | Kozikode | ESD_SOFT_SOFT FROM OIC | ESD_SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD_SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1892 | Kozikode | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1892 | Kozikode | LP 02_BC-01B_BS VI HSD | LP 02 | TLF | BC-01B | BS VI HSD | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  | 0
1892 | Kozikode | LP 03_BC-02A_BS VI MS | LP 03 | TLF | BC-02A | BS VI MS | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1892 | Kozikode | LP 04_BC-02B_BS VI HSD | LP 04 | TLF | BC-02B | BS VI HSD | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  | 0
1892 | Kozikode | LP 05_BC-03A_BS VI MS | LP 05 | TLF | BC-03A | BS VI MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1892 | Kozikode | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  | 0
1892 | Kozikode | LP 07_BC-04A_BS VI MS | LP 07 | TLF | BC-04A | BS VI MS | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1892 | Kozikode | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  | 0 | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  | 0
1892 | Kozikode | LP 09_BC-05A_BS VI HSD | LP 09 | TLF | BC-05A | BS VI HSD | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  | 0
1892 | Kozikode | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1892 | Kozikode | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1892 | Kozikode | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1892 | Kozikode | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1892 | Kozikode | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1892 | Kozikode | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1892 | Kozikode | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1892 | Kozikode | Gantry Permissive Off |  |  | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1892 | Kozikode | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1892 | Kozikode | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 1 | PUMP.FWP-02.REMOTE_STATUS | 1 | PUMP.FWP-03.REMOTE_STATUS | 1 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.PT-02.PRESSURE |  | PressureTransmitter.PT-01.PRESSURE |  | PLC.SFTPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1