## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH | Normal value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Normal value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal value | Sensor_Id | Sensor_Type | RADAR HHH | Normal value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1919 | Secunderabad | 51-TT-CR-003D_BS VI HSD | 51-TT-CR-003D | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-003D.LEVEL |  | 51-TT-CR-003D | Primary Radar | TANK.51-TT-CR-003D.TANK_ALERT | 0 | TANK.51-TT-CR-003D.HIGH_LEVEL | 0 | 51-TT-CR-003D | Primary Radar | TANK.51-TT-CR-003D.HIGH_HIGH_LEVEL | 0 | 51-TT-CR-003D | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_OPEN | 0 | ROSOV-15 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV OL | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1307.CLOSE_STATUS | 1 | MOV-1307 | MOV IL1 |  |  | MOV.MOV-1308.CLOSE_STATUS | 1 | MOV-1308 | MOV OL
1919 | Secunderabad | 51-TT-CR-005A_ETHANOL | 51-TT-CR-005A | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-005A.LEVEL |  | 51-TT-CR-005A | Primary Radar | TANK.51-TT-CR-005A.TANK_ALERT | 0 | TANK.51-TT-CR-005A.HIGH_LEVEL | 0 | 51-TT-CR-005A | Primary Radar | TANK.51-TT-CR-005A.HIGH_HIGH_LEVEL | 0 | 51-TT-CR-005A | Primary Radar | LEVELSWITCH.LSW-17.SWITCH_STATUS | 0 | LSW-17 | VFT | LEVELSWITCH.LSW-17.PROOF_TEST_OK | 0 | LSW-17 | VFT | LEVELSWITCH.LSW-17.PROOF_TEST_FAILED | 0 | LSW-17 | VFT | LEVELSWITCH.RDR-17.SWITCH_STATUS | 0 | RDR-17 | RADAR | LEVELSWITCH.RDR-17.PROOF_TEST_OK | 0 | RDR-17 | RADAR | LEVELSWITCH.RDR-17.PROOF_TEST_FAILED | 0 | RDR-17 | RADAR | MOV.ROSOV-33.OPEN_STATUS | 0 | ROSOV-33 | ROSOV IL1 | MOV.ROSOV-33.FAILED_TO_OPEN | 0 | ROSOV-33 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-23.FAILED_TO_CLOSE | 0 | ROSOV-23 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1506.CLOSE_STATUS | 1 | MOV-1506 | MOV IL1 |  |  | MOV.MOV-1513.CLOSE_STATUS | 1 | MOV-1513 | MOV OL
1919 | Secunderabad | 51-TT-CR-005B_INTERFACE | 51-TT-CR-005B | AG | INTERFACE | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-005B.LEVEL |  | 51-TT-CR-005B | Primary Radar | TANK.51-TT-CR-005B.TANK_ALERT | 0 | TANK.51-TT-CR-005B.HIGH_LEVEL | 0 | 51-TT-CR-005B | Primary Radar | TANK.51-TT-CR-005B.HIGH_HIGH_LEVEL | 0 | 51-TT-CR-005B | Primary Radar | LEVELSWITCH.LSW-15.SWITCH_STATUS | 0 | LSW-15 | VFT | LEVELSWITCH.LSW-15.PROOF_TEST_OK | 0 | LSW-15 | VFT | LEVELSWITCH.LSW-15.PROOF_TEST_FAILED | 0 | LSW-15 | VFT | LEVELSWITCH.RDR-15.SWITCH_STATUS | 0 | RDR-15 | RADAR | LEVELSWITCH.RDR-15.PROOF_TEST_OK | 0 | RDR-15 | RADAR | LEVELSWITCH.RDR-15.PROOF_TEST_FAILED | 0 | RDR-15 | RADAR | [12 empty] | MOV.ROSOV-30.OPEN_STATUS | 0 | ROSOV-30 | ROSOV OL | MOV.ROSOV-30.FAILED_TO_CLOSE | 0 | ROSOV-30 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1508.CLOSE_STATUS | 1 | MOV-1508 | MOV IL1 |  |  |  | 1
1919 | Secunderabad | 51-TT-CR-006A_WATER | 51-TT-CR-006A | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-006A.LEVEL |  | 51-TT-CR-006A | Primary Radar | TANK.51-TT-CR-006A.TANK_ALERT | 0
1919 | Secunderabad | 51-TT-CR-006B_WATER | 51-TT-CR-006B | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-006B.LEVEL |  | 51-TT-CR-006B | Primary Radar | TANK.51-TT-CR-006B.TANK_ALERT | 0
1919 | Secunderabad | 51-TT-CR-006C_WATER | 51-TT-CR-006C | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-006C.LEVEL |  | 51-TT-CR-006C | Primary Radar | TANK.51-TT-CR-006C.TANK_ALERT | 0
1919 | Secunderabad | 51-TT-CR-006D_WATER | 51-TT-CR-006D | AG | WATER | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-CR-006D.LEVEL |  | 51-TT-CR-006D | Primary Radar | TANK.51-TT-CR-006D.TANK_ALERT | 0
1919 | Secunderabad | 51-TT-FR-001A_BS VI MS | 51-TT-FR-001A | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-001A.LEVEL |  | 51-TT-FR-001A | Primary Radar | TANK.51-TT-FR-001A.TANK_ALERT | 0 | TANK.51-TT-FR-001A.HIGH_LEVEL | 0 | 51-TT-FR-001A | Primary Radar | TANK.51-TT-FR-001A.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-001A | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_OPEN | 0 | ROSOV-05 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1101.CLOSE_STATUS | 1 | MOV-1101 | MOV IL1 |  |  | MOV.MOV-1103.CLOSE_STATUS | 1 | MOV-1103 | MOV OL |  |  | RIMSEAL.RIMSEAL-01.FIRE_ALARM | 0 | RIMSEAL-01 | RIMSEAL | RIMSEAL.RIMSEAL-01.DETECTOR_FAULT | 0 | RIMSEAL-01 | RIMSEAL
1919 | Secunderabad | 51-TT-FR-001B_BS VI MS | 51-TT-FR-001B | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-001B.LEVEL |  | 51-TT-FR-001B | Primary Radar | TANK.51-TT-FR-001B.TANK_ALERT | 0 | TANK.51-TT-FR-001B.HIGH_LEVEL | 0 | 51-TT-FR-001B | Primary Radar | TANK.51-TT-FR-001B.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-001B | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_OPEN | 0 | ROSOV-01 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1102.CLOSE_STATUS | 1 | MOV-1102 | MOV IL1 |  |  | MOV.MOV-1104.CLOSE_STATUS | 1 | MOV-1104 | MOV OL |  |  | RIMSEAL.RIMSEAL-02.FIRE_ALARM | 0 | RIMSEAL-02 | RIMSEAL | RIMSEAL.RIMSEAL-02.DETECTOR_FAULT | 0 | RIMSEAL-02 | RIMSEAL
1919 | Secunderabad | 51-TT-FR-001C_GASOHOL | 51-TT-FR-001C | AG | GASOHOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-001C.LEVEL |  | 51-TT-FR-001C | Primary Radar | TANK.51-TT-FR-001C.TANK_ALERT | 0 | TANK.51-TT-FR-001C.HIGH_LEVEL | 0 | 51-TT-FR-001C | Primary Radar | TANK.51-TT-FR-001C.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-001C | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_OPEN | 0 | ROSOV-07 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1105.CLOSE_STATUS | 1 | MOV-1105 | MOV IL1 |  |  | MOV.MOV-1107.CLOSE_STATUS | 1 | MOV-1107 | MOV OL |  |  | RIMSEAL.RIMSEAL-03.FIRE_ALARM | 0 | RIMSEAL-03 | RIMSEAL | RIMSEAL.RIMSEAL-03.DETECTOR_FAULT | 0 | RIMSEAL-03 | RIMSEAL
1919 | Secunderabad | 51-TT-FR-001D_INTERFACE | 51-TT-FR-001D | AG | INTERFACE | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-001D.LEVEL |  | 51-TT-FR-001D | Primary Radar | TANK.51-TT-FR-001D.TANK_ALERT | 0 | TANK.51-TT-FR-001D.HIGH_LEVEL | 0 | 51-TT-FR-001D | Primary Radar | TANK.51-TT-FR-001D.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-001D | Primary Radar | LEVELSWITCH.LSW-12.SWITCH_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_OK | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_FAILED | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.SWITCH_STATUS | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_OK | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_FAILED | 0 | RDR-12 | RADAR | [12 empty] | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV OL | MOV.ROSOV-24.FAILED_TO_CLOSE | 0 | ROSOV-24 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1106.CLOSE_STATUS | 1 | MOV-1106 | MOV IL1 |  |  | MOV.MOV-1108.CLOSE_STATUS | 1 | MOV-1108 | MOV OL
1919 | Secunderabad | 51-TT-FR-002A_SKO | 51-TT-FR-002A | AG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-002A.LEVEL |  | 51-TT-FR-002A | Primary Radar | TANK.51-TT-FR-002A.TANK_ALERT | 0 | TANK.51-TT-FR-002A.HIGH_LEVEL | 0 | 51-TT-FR-002A | Primary Radar | TANK.51-TT-FR-002A.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-002A | Primary Radar | LEVELSWITCH.LSW-13.SWITCH_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_OK | 0 | LSW-13 | VFT | LEVELSWITCH.LSW-13.PROOF_TEST_FAILED | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.SWITCH_STATUS | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_OK | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_FAILED | 0 | RDR-13 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_OPEN | 0 | ROSOV-25 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-26.OPEN_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | 0 | ROSOV-26 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1201.CLOSE_STATUS | 1 | MOV-1201 | MOV IL1 |  |  | MOV.MOV-1204.CLOSE_STATUS | 1 | MOV-1204 | MOV OL
1919 | Secunderabad | 51-TT-FR-002B_BS VI HSD | 51-TT-FR-002B | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-002B.LEVEL |  | 51-TT-FR-002B | Primary Radar |  |  | TANK.51-TT-FR-002B.HIGH_LEVEL | 0 | 51-TT-FR-002B | Primary Radar | TANK.51-TT-FR-002B.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-002B | Primary Radar | LEVELSWITCH.LSW-14.SWITCH_STATUS | 0 | LSW-14 | VFT | LEVELSWITCH.LSW-14.PROOF_TEST_OK | 0 | LSW-14 | VFT | LEVELSWITCH.LSW-14.PROOF_TEST_FAILED | 0 | LSW-14 | VFT | LEVELSWITCH.RDR-14.SWITCH_STATUS | 0 | RDR-14 | RADAR | LEVELSWITCH.RDR-14.PROOF_TEST_OK | 0 | RDR-14 | RADAR | LEVELSWITCH.RDR-14.PROOF_TEST_FAILED | 0 | RDR-14 | RADAR | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV IL1 | MOV.ROSOV-27.FAILED_TO_OPEN | 0 | ROSOV-27 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-28.OPEN_STATUS | 0 | ROSOV-28 | ROSOV OL | MOV.ROSOV-28.FAILED_TO_CLOSE | 0 | ROSOV-28 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1202.CLOSE_STATUS | 1 | MOV-1202 | MOV IL1 |  |  | MOV.MOV-1205.CLOSE_STATUS | 1 | MOV-1205 | MOV OL
1919 | Secunderabad | 51-TT-FR-003A_BS VI HSD | 51-TT-FR-003A | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-003A.LEVEL |  | 51-TT-FR-003A | Primary Radar | TANK.51-TT-FR-003A.TANK_ALERT | 0 | TANK.51-TT-FR-003A.HIGH_LEVEL | 0 | 51-TT-FR-003A | Primary Radar | TANK.51-TT-FR-003A.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-003A | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV IL1 | MOV.ROSOV-17.FAILED_TO_OPEN | 0 | ROSOV-17 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV OL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1301.CLOSE_STATUS | 1 | MOV-1301 | MOV IL1 |  |  | MOV.MOV-1303.CLOSE_STATUS | 1 | MOV-1303 | MOV OL
1919 | Secunderabad | 51-TT-FR-003B_BS VI HSD | 51-TT-FR-003B | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-003B.LEVEL |  | 51-TT-FR-003B | Primary Radar | TANK.51-TT-FR-003B.TANK_ALERT | 0 | TANK.51-TT-FR-003B.HIGH_LEVEL | 0 | 51-TT-FR-003B | Primary Radar | TANK.51-TT-FR-003B.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-003B | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_OPEN | 0 | ROSOV-11 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1302.CLOSE_STATUS | 1 | MOV-1302 | MOV IL1 |  |  | MOV.MOV-1304.CLOSE_STATUS | 1 | MOV-1304 | MOV OL
1919 | Secunderabad | 51-TT-FR-003C_ETHANOL | 51-TT-FR-003C | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-003C.LEVEL |  | 51-TT-FR-003C | Primary Radar | TANK.51-TT-FR-003C.TANK_ALERT | 0 | TANK.51-TT-FR-003C.HIGH_LEVEL | 0 | 51-TT-FR-003C | Primary Radar | TANK.51-TT-FR-003C.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-003C | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_OPEN | 0 | ROSOV-03 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1305.CLOSE_STATUS | 1 | MOV-1305 | MOV IL1 |  |  | MOV.MOV-1306.CLOSE_STATUS | 1 | MOV-1306 | MOV OL |  |  | RIMSEAL.RIMSEAL-04.FIRE_ALARM | 0 | RIMSEAL-04 | RIMSEAL | RIMSEAL.RIMSEAL-04.DETECTOR_FAULT | 0 | RIMSEAL-04 | RIMSEAL
1919 | Secunderabad | 51-TT-FR-003E_BS VI HSD | 51-TT-FR-003E | AG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-003E.LEVEL |  | 51-TT-FR-003E | Primary Radar | TANK.51-TT-FR-003E.TANK_ALERT | 0 | TANK.51-TT-FR-003E.HIGH_LEVEL | 0 | 51-TT-FR-003E | Primary Radar | TANK.51-TT-FR-003E.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-003E | Primary Radar | LEVELSWITCH.LSW-11.SWITCH_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_OK | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_FAILED | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.SWITCH_STATUS | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_OK | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_FAILED | 0 | RDR-11 | RADAR | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV IL1 | MOV.ROSOV-21.FAILED_TO_OPEN | 0 | ROSOV-21 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV OL | MOV.ROSOV-22.FAILED_TO_CLOSE | 0 | ROSOV-22 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1309.CLOSE_STATUS | 1 | MOV-1309 | MOV IL1 |  |  | MOV.MOV-1310.CLOSE_STATUS | 1 | MOV-1310 | MOV OL
1919 | Secunderabad | 51-TT-FR-004A_ATF | 51-TT-FR-004A | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-004A.LEVEL |  | 51-TT-FR-004A | Primary Radar | TANK.51-TT-FR-004A.TANK_ALERT | 0 | TANK.51-TT-FR-004A.HIGH_LEVEL | 0 | 51-TT-FR-004A | Primary Radar | TANK.51-TT-FR-004A.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-004A | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_OPEN | 0 | ROSOV-13 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1401.CLOSE_STATUS | 1 | MOV-1401 | MOV IL1 |  |  | MOV.MOV-1404.CLOSE_STATUS | 1 | MOV-1404 | MOV OL
1919 | Secunderabad | 51-TT-FR-004B_ATF | 51-TT-FR-004B | AG | ATF | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-004B.LEVEL |  | 51-TT-FR-004B | Primary Radar | TANK.51-TT-FR-004B.TANK_ALERT | 0 | TANK.51-TT-FR-004B.HIGH_LEVEL | 0 | 51-TT-FR-004B | Primary Radar | TANK.51-TT-FR-004B.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-004B | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_OPEN | 0 | ROSOV-19 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1402.CLOSE_STATUS | 1 | MOV-1402 | MOV IL1 |  |  | MOV.MOV-1405.CLOSE_STATUS | 1 | MOV-1405 | MOV OL
1919 | Secunderabad | 51-TT-FR-004C_BS VI MS | 51-TT-FR-004C | AG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-004C.LEVEL |  | 51-TT-FR-004C | Primary Radar | TANK.51-TT-FR-004C.TANK_ALERT | 0 | TANK.51-TT-FR-004C.HIGH_LEVEL | 0 | 51-TT-FR-004C | Primary Radar | TANK.51-TT-FR-004C.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-004C | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_OPEN | 0 | ROSOV-09 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1403.CLOSE_STATUS | 1 | MOV-1403 | MOV IL1 |  |  | MOV.MOV-1406.CLOSE_STATUS | 1 | MOV-1406 | MOV OL |  |  | RIMSEAL.RIMSEAL-05.FIRE_ALARM | 0 | RIMSEAL-05 | RIMSEAL | RIMSEAL.RIMSEAL-05.DETECTOR_FAULT | 0 | RIMSEAL-05 | RIMSEAL
1919 | Secunderabad | 51-TT-FR-005C_ETHANOL | 51-TT-FR-005C | AG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-FR-005C.LEVEL |  | 51-TT-FR-005C | Primary Radar | TANK.51-TT-FR-005C.TANK_ALERT | 0 | TANK.51-TT-FR-005C.HIGH_LEVEL | 0 | 51-TT-FR-005C | Primary Radar | TANK.51-TT-FR-005C.HIGH_HIGH_LEVEL | 0 | 51-TT-FR-005C | Primary Radar | LEVELSWITCH.LSW-16.SWITCH_STATUS | 0 | LSW-16 | VFT | LEVELSWITCH.LSW-16.PROOF_TEST_OK | 0 | LSW-16 | VFT | LEVELSWITCH.LSW-16.PROOF_TEST_FAILED | 0 | LSW-16 | VFT | LEVELSWITCH.RDR-16.SWITCH_STATUS | 0 | RDR-16 | RADAR | LEVELSWITCH.RDR-16.PROOF_TEST_OK | 0 | RDR-16 | RADAR | LEVELSWITCH.RDR-16.PROOF_TEST_FAILED | 0 | RDR-16 | RADAR | MOV.ROSOV-31.OPEN_STATUS | 0 | ROSOV-31 | ROSOV IL1 | MOV.ROSOV-31.FAILED_TO_OPEN | 0 | ROSOV-31 | ROSOV FAILED IL1 |  |  |  |  | MOV.ROSOV-32.OPEN_STATUS | 0 | ROSOV-32 | ROSOV OL | MOV.ROSOV-32.FAILED_TO_CLOSE | 0 | ROSOV-32 | ROSOV FAILED OL |  |  |  |  | MOV.MOV-1510.CLOSE_STATUS | 1 | MOV-1510 | MOV IL1 |  |  | MOV.MOV-1511.CLOSE_STATUS | 1 | MOV-1511 | MOV OL
1919 | Secunderabad | 51-TT-UG-0001_BS VI MS | 51-TT-UG-0001 | UG | BS VI MS | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0001.LEVEL |  | 51-TT-UG-0001 | Primary Radar | TANK.51-TT-UG-0001.TANK_ALERT | 0 | TANK.51-TT-UG-0001.HIGH_LEVEL | 0 | 51-TT-UG-0001 | Primary Radar | TANK.51-TT-UG-0001.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0001 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0002_SKO | 51-TT-UG-0002 | UG | SKO | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0002.LEVEL |  | 51-TT-UG-0002 | Primary Radar | TANK.51-TT-UG-0002.TANK_ALERT | 0 | TANK.51-TT-UG-0002.HIGH_LEVEL | 0 | 51-TT-UG-0002 | Primary Radar | TANK.51-TT-UG-0002.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0002 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0003_BS VI HSD | 51-TT-UG-0003 | UG | BS VI HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0003.LEVEL |  | 51-TT-UG-0003 | Primary Radar | TANK.51-TT-UG-0003.TANK_ALERT | 0 | TANK.51-TT-UG-0003.HIGH_LEVEL | 0 | 51-TT-UG-0003 | Primary Radar | TANK.51-TT-UG-0003.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0003 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0010_ETHANOL | 51-TT-UG-0010 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0010.LEVEL |  | 51-TT-UG-0010 | Primary Radar | TANK.51-TT-UG-0010.TANK_ALERT | 0 | TANK.51-TT-UG-0010.HIGH_LEVEL | 0 | 51-TT-UG-0010 | Primary Radar | TANK.51-TT-UG-0010.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0010 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0013_ETHANOL | 51-TT-UG-0013 | UG | ETHANOL | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0013.LEVEL |  | 51-TT-UG-0013 | Primary Radar | TANK.51-TT-UG-0013.TANK_ALERT | 0 | TANK.51-TT-UG-0013.HIGH_LEVEL | 0 | 51-TT-UG-0013 | Primary Radar | TANK.51-TT-UG-0013.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0013 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0014_BIO HSD | 51-TT-UG-0014 | UG | BIO HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0014.LEVEL |  | 51-TT-UG-0014 | Primary Radar | TANK.51-TT-UG-0014.TANK_ALERT | 0 | TANK.51-TT-UG-0014.HIGH_LEVEL | 0 | 51-TT-UG-0014 | Primary Radar | TANK.51-TT-UG-0014.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0014 | Primary Radar
1919 | Secunderabad | 51-TT-UG-0015_BIO HSD | 51-TT-UG-0015 | UG | BIO HSD | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0 | TANK.51-TT-UG-0015.LEVEL |  | 51-TT-UG-0015 | Primary Radar | TANK.51-TT-UG-0015.TANK_ALERT | 0 | TANK.51-TT-UG-0015.HIGH_LEVEL | 0 | 51-TT-UG-0015 | Primary Radar | TANK.51-TT-UG-0015.HIGH_HIGH_LEVEL | 0 | 51-TT-UG-0015 | Primary Radar
1919 | Secunderabad | 51-TT-UG-SLOP_SLOP | 51-TT-UG-SLOP | UG | SLOP | PLC.SFTPLC.CAUSE_ANY_ESD_PB_ACTI | 0

## Tank Maintenance
SAPID | Location | Device Name |  | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | ROSOV MAINTENANCE OL | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | MOV MAINTENANCE RCL | Normal Value | MOV MAINTENANCE OL | Normal Value | Sensor_Id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal value
1919 | Secunderabad_M | 51-TT-CR-003D_BS VI HSD | 51-TT-CR-003D_BS VI HSD@Secunderabad_M | 51-TT-CR-003D | AG | BS VI HSD | TANK.51-TT-CR-003D.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV IL1 |  |  | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV OL |  |  | MOV.MOV-1307.MAINTENANCE_STATUS | 0 | MOV-1307 | MOV IL1 |  |  |  |  | MOV.MOV-1308.MAINTENANCE_STATUS | 0 | MOV-1308 | MOV OL
1919 | Secunderabad_M | 51-TT-CR-005A_ETHANOL | 51-TT-CR-005A_ETHANOL@Secunderabad_M | 51-TT-CR-005A | AG | ETHANOL | TANK.51-TT-CR-005A.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-17.MAINTENANCE_STATUS | 0 | LSW-17 | VFT | LEVELSWITCH.RDR-17.MAINTENANCE_STATUS | 0 | RDR-17 | RADAR | MOV.ROSOV-33.MAINTENANCE_STATUS | 0 | ROSOV-33 | ROSOV IL1 |  |  | MOV.ROSOV-23.MAINTENANCE_STATUS | 0 | ROSOV-23 | ROSOV OL |  |  | MOV.MOV-1506.MAINTENANCE_STATUS | 0 | MOV-1506 | MOV IL1 |  |  |  |  | MOV.MOV-1513.MAINTENANCE_STATUS | 0 | MOV-1513 | MOV OL
1919 | Secunderabad_M | 51-TT-CR-005B_INTERFACE | 51-TT-CR-005B_INTERFACE@Secunderabad_M | 51-TT-CR-005B | AG | INTERFACE | TANK.51-TT-CR-005B.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-15.MAINTENANCE_STATUS | 0 | LSW-15 | VFT | LEVELSWITCH.RDR-15.MAINTENANCE_STATUS | 0 | RDR-15 | RADAR | [12 empty] | MOV.MOV-1508.MAINTENANCE_STATUS | 0 | MOV-1508 | MOV IL1
1919 | Secunderabad_M | 51-TT-CR-006A_WATER | 51-TT-CR-006A_WATER@Secunderabad_M | 51-TT-CR-006A | AG | WATER
1919 | Secunderabad_M | 51-TT-CR-006B_WATER | 51-TT-CR-006B_WATER@Secunderabad_M | 51-TT-CR-006B | AG | WATER
1919 | Secunderabad_M | 51-TT-CR-006C_WATER | 51-TT-CR-006C_WATER@Secunderabad_M | 51-TT-CR-006C | AG | WATER
1919 | Secunderabad_M | 51-TT-CR-006D_WATER | 51-TT-CR-006D_WATER@Secunderabad_M | 51-TT-CR-006D | AG | WATER
1919 | Secunderabad_M | 51-TT-FR-001A_BS VI MS | 51-TT-FR-001A_BS VI MS@Secunderabad_M | 51-TT-FR-001A | AG | BS VI MS | TANK.51-TT-FR-001A.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV IL1 |  |  | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV OL |  |  | MOV.MOV-1101.MAINTENANCE_STATUS | 0 | MOV-1101 | MOV IL1 |  |  |  |  | MOV.MOV-1103.MAINTENANCE_STATUS | 0 | MOV-1103 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-001B_BS VI MS | 51-TT-FR-001B_BS VI MS@Secunderabad_M | 51-TT-FR-001B | AG | BS VI MS | TANK.51-TT-FR-001B.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL |  |  | MOV.MOV-1102.MAINTENANCE_STATUS | 0 | MOV-1102 | MOV IL1 |  |  |  |  | MOV.MOV-1104.MAINTENANCE_STATUS | 0 | MOV-1104 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-001C_GASOHOL | 51-TT-FR-001C_GASOHOL@Secunderabad_M | 51-TT-FR-001C | AG | GASOHOL | TANK.51-TT-FR-001C.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL |  |  | MOV.MOV-1105.MAINTENANCE_STATUS | 0 | MOV-1105 | MOV IL1 |  |  |  |  | MOV.MOV-1107.MAINTENANCE_STATUS | 0 | MOV-1107 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-001D_INTERFACE | 51-TT-FR-001D_INTERFACE@Secunderabad_M | 51-TT-FR-001D | AG | INTERFACE | TANK.51-TT-FR-001D.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-12.MAINTENANCE_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.MAINTENANCE_STATUS | 0 | RDR-12 | RADAR | [6 empty] | MOV.ROSOV-24.MAINTENANCE_STATUS | 0 | ROSOV-24 | ROSOV OL |  |  | MOV.MOV-1106.MAINTENANCE_STATUS | 0 | MOV-1106 | MOV IL1 |  |  |  |  | MOV.MOV-1108.MAINTENANCE_STATUS | 0 | MOV-1108 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-002A_SKO | 51-TT-FR-002A_SKO@Secunderabad_M | 51-TT-FR-002A | AG | SKO | TANK.51-TT-FR-002A.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-13.MAINTENANCE_STATUS | 0 | LSW-13 | VFT | LEVELSWITCH.RDR-13.MAINTENANCE_STATUS | 0 | RDR-13 | RADAR | MOV.ROSOV-25.MAINTENANCE_STATUS | 0 | ROSOV-25 | ROSOV IL1 |  |  | MOV.ROSOV-26.MAINTENANCE_STATUS | 0 | ROSOV-26 | ROSOV OL |  |  | MOV.MOV-1201.MAINTENANCE_STATUS | 0 | MOV-1201 | MOV IL1 |  |  |  |  | MOV.MOV-1204.MAINTENANCE_STATUS | 0 | MOV-1204 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-002B_BS VI HSD | 51-TT-FR-002B_BS VI HSD@Secunderabad_M | 51-TT-FR-002B | AG | BS VI HSD | TANK.51-TT-FR-002B.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-14.MAINTENANCE_STATUS | 0 | LSW-14 | VFT | LEVELSWITCH.RDR-14.MAINTENANCE_STATUS | 0 | RDR-14 | RADAR | MOV.ROSOV-27.MAINTENANCE_STATUS | 0 | ROSOV-27 | ROSOV IL1 |  |  | MOV.ROSOV-28.MAINTENANCE_STATUS | 0 | ROSOV-28 | ROSOV OL |  |  | MOV.MOV-1202.MAINTENANCE_STATUS | 0 | MOV-1202 | MOV IL1 |  |  |  |  | MOV.MOV-1205.MAINTENANCE_STATUS | 0 | MOV-1205 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-003A_BS VI HSD | 51-TT-FR-003A_BS VI HSD@Secunderabad_M | 51-TT-FR-003A | AG | BS VI HSD | TANK.51-TT-FR-003A.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV IL1 |  |  | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV OL |  |  | MOV.MOV-1301.MAINTENANCE_STATUS | 0 | MOV-1301 | MOV IL1 |  |  |  |  | MOV.MOV-1303.MAINTENANCE_STATUS | 0 | MOV-1303 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-003B_BS VI HSD | 51-TT-FR-003B_BS VI HSD@Secunderabad_M | 51-TT-FR-003B | AG | BS VI HSD | TANK.51-TT-FR-003B.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV IL1 |  |  | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV OL |  |  | MOV.MOV-1302.MAINTENANCE_STATUS | 0 | MOV-1302 | MOV IL1 |  |  |  |  | MOV.MOV-1304.MAINTENANCE_STATUS | 0 | MOV-1304 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-003C_ETHANOL | 51-TT-FR-003C_ETHANOL@Secunderabad_M | 51-TT-FR-003C | AG | ETHANOL | TANK.51-TT-FR-003C.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV IL1 |  |  | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV OL |  |  | MOV.MOV-1305.MAINTENANCE_STATUS | 0 | MOV-1305 | MOV IL1 |  |  |  |  | MOV.MOV-1306.MAINTENANCE_STATUS | 0 | MOV-1306 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-003E_BS VI HSD | 51-TT-FR-003E_BS VI HSD@Secunderabad_M | 51-TT-FR-003E | AG | BS VI HSD | TANK.51-TT-FR-003E.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-11.MAINTENANCE_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.MAINTENANCE_STATUS | 0 | RDR-11 | RADAR | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV IL1 |  |  | MOV.ROSOV-22.MAINTENANCE_STATUS | 0 | ROSOV-22 | ROSOV OL |  |  | MOV.MOV-1309.MAINTENANCE_STATUS | 0 | MOV-1309 | MOV IL1 |  |  |  |  | MOV.MOV-1310.MAINTENANCE_STATUS | 0 | MOV-1310 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-004A_ATF | 51-TT-FR-004A_ATF@Secunderabad_M | 51-TT-FR-004A | AG | ATF | TANK.51-TT-FR-004A.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL |  |  | MOV.MOV-1401.MAINTENANCE_STATUS | 0 | MOV-1401 | MOV IL1 |  |  |  |  | MOV.MOV-1404.MAINTENANCE_STATUS | 0 | MOV-1404 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-004B_ATF | 51-TT-FR-004B_ATF@Secunderabad_M | 51-TT-FR-004B | AG | ATF | TANK.51-TT-FR-004B.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL |  |  | MOV.MOV-1402.MAINTENANCE_STATUS | 0 | MOV-1402 | MOV IL1 |  |  |  |  | MOV.MOV-1405.MAINTENANCE_STATUS | 0 | MOV-1405 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-004C_BS VI MS | 51-TT-FR-004C_BS VI MS@Secunderabad_M | 51-TT-FR-004C | AG | BS VI MS | TANK.51-TT-FR-004C.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV OL |  |  | MOV.MOV-1403.MAINTENANCE_STATUS | 0 | MOV-1403 | MOV IL1 |  |  |  |  | MOV.MOV-1406.MAINTENANCE_STATUS | 0 | MOV-1406 | MOV OL
1919 | Secunderabad_M | 51-TT-FR-005C_ETHANOL | 51-TT-FR-005C_ETHANOL@Secunderabad_M | 51-TT-FR-005C | AG | ETHANOL | TANK.51-TT-FR-005C.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-16.MAINTENANCE_STATUS | 0 | LSW-16 | VFT | LEVELSWITCH.RDR-16.MAINTENANCE_STATUS | 0 | RDR-16 | RADAR | MOV.ROSOV-31.MAINTENANCE_STATUS | 0 | ROSOV-31 | ROSOV IL1 |  |  | MOV.ROSOV-32.MAINTENANCE_STATUS | 0 | ROSOV-32 | ROSOV OL |  |  | MOV.MOV-1510.MAINTENANCE_STATUS | 0 | MOV-1510 | MOV IL1 |  |  |  |  | MOV.MOV-1511.MAINTENANCE_STATUS | 0 | MOV-1511 | MOV OL

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | Normal value | PUMP OFF STATUS | Normal value | PUMP LR STATUS | Normal value
1919 | Secunderabad | 51-PA-CF-001A_BS VI MS_DISPATCH | 51-PA-CF-001A | BS VI MS | TLF | DISPATCH | PUMP.51-PA-CF-001A.ON | 1 | PUMP.51-PA-CF-001A.OFF | 0 | PUMP.51-PA-CF-001A.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-001B_BS VI MS_DISPATCH | 51-PA-CF-001B | BS VI MS | TLF | DISPATCH | PUMP.51-PA-CF-001B.ON | 1 | PUMP.51-PA-CF-001B.OFF | 0 | PUMP.51-PA-CF-001B.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-001C_BS VI MS_DISPATCH | 51-PA-CF-001C | BS VI MS | TLF | DISPATCH | PUMP.51-PA-CF-001C.ON | 1 | PUMP.51-PA-CF-001C.OFF | 0 | PUMP.51-PA-CF-001C.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-001E_ATF_DISPATCH | 51-PA-CF-001E | ATF | TLF | DISPATCH | PUMP.51-PA-CF-001E.ON | 1 | PUMP.51-PA-CF-001E.OFF | 0 | PUMP.51-PA-CF-001E.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-001F_ATF_DISPATCH | 51-PA-CF-001F | ATF | TLF | DISPATCH | PUMP.51-PA-CF-001F.ON | 1 | PUMP.51-PA-CF-001F.OFF | 0 | PUMP.51-PA-CF-001F.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003A_BS VI HSD_DISPATCH | 51-PA-CF-003A | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003A.ON | 1 | PUMP.51-PA-CF-003A.OFF | 0 | PUMP.51-PA-CF-003A.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003B_BS VI HSD_DISPATCH | 51-PA-CF-003B | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003B.ON | 1 | PUMP.51-PA-CF-003B.OFF | 0 | PUMP.51-PA-CF-003B.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003C_BS VI HSD_DISPATCH | 51-PA-CF-003C | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003C.ON | 1 | PUMP.51-PA-CF-003C.OFF | 0 | PUMP.51-PA-CF-003C.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003D_BS VI HSD_DISPATCH | 51-PA-CF-003D | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003D.ON | 1 | PUMP.51-PA-CF-003D.OFF | 0 | PUMP.51-PA-CF-003D.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003E_BS VI HSD_DISPATCH | 51-PA-CF-003E | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003E.ON | 1 | PUMP.51-PA-CF-003E.OFF | 0 | PUMP.51-PA-CF-003E.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-003F_BS VI HSD_DISPATCH | 51-PA-CF-003F | BS VI HSD | TLF | DISPATCH | PUMP.51-PA-CF-003F.ON | 1 | PUMP.51-PA-CF-003F.OFF | 0 | PUMP.51-PA-CF-003F.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-006A_SUMP_DISPATCH | 51-PA-CF-006A | SUMP | TLF | DISPATCH | PUMP.51-PA-CF-003F.ON | 1 | PUMP.51-PA-CF-003F.OFF | 0 | PUMP.51-PA-CF-003F.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-006B_SUMP_DISPATCH | 51-PA-CF-006B | SUMP | TLF | DISPATCH | PUMP.51-PA-CF-006B.ON | 1 | PUMP.51-PA-CF-006B.OFF | 0 | PUMP.51-PA-CF-006B.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-006C_SUMP_DISPATCH | 51-PA-CF-006C | SUMP | TLF | DISPATCH | PUMP.51-PA-CF-006C.ON | 1 | PUMP.51-PA-CF-006C.OFF | 0 | PUMP.51-PA-CF-006C.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-CF-007_SUMP_DISPATCH | 51-PA-CF-007 | SUMP | TLF | DISPATCH | PUMP.51-PA-CF-007.ON | 1 | PUMP.51-PA-CF-007.OFF | 0 | PUMP.51-PA-CF-007.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-HEXANE-13_HEXANE_DISPATCH | 51-PA-HEXANE-13 | HEXANE | TLF | DISPATCH | PUMP.51-PA-HEXANE-13.ON | 1 | PUMP.51-PA-HEXANE-13.OFF | 0 | PUMP.51-PA-HEXANE-13.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-HEXANE-14_SUMP_DISPATCH | 51-PA-HEXANE-14 | SUMP | TLF | DISPATCH | PUMP.51-PA-HEXANE-14.ON | 1 | PUMP.51-PA-HEXANE-14.OFF | 0 | PUMP.51-PA-HEXANE-14.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-MTO-15_MTO_DISPATCH | 51-PA-MTO-15 | MTO | TLF | DISPATCH | PUMP.51-PA-MTO-15.ON | 1 | PUMP.51-PA-MTO-15.OFF | 0 | PUMP.51-PA-MTO-15.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-RP-9A_POWER100_DISPATCH | 51-PA-RP-9A | POWER100 | TLF | DISPATCH | PUMP.51-PA-RP-9A.ON | 1 | PUMP.51-PA-RP-9A.OFF | 0 | PUMP.51-PA-RP-9A.REMOTE_STATUS | 0
1919 | Secunderabad | 51-PA-RP-9B_POWER100_DISPATCH | 51-PA-RP-9B | POWER100 | TLF | DISPATCH | PUMP.51-PA-RP-9B.ON | 1 | PUMP.51-PA-RP-9B.OFF | 0 | PUMP.51-PA-RP-9B.REMOTE_STATUS | 0
1919 | Secunderabad | ADTV PMP-1 POWER_POWER_DISPATCH | ADTV PMP-1 POWER | POWER | TLF | DISPATCH | PUMP.ADTV PMP-1 POWER.ON | 1 | PUMP.ADTV PMP-1 POWER.OFF | 0 | PUMP.ADTV PMP-1 POWER.REMOTE_STATUS | 0
1919 | Secunderabad | ADTV PMP-1 TURBO_TURBO_DISPATCH | ADTV PMP-1 TURBO | TURBO | TLF | DISPATCH | PUMP.ADTV PMP-1 TURBO.ON | 1 | PUMP.ADTV PMP-1 TURBO.OFF | 0 | PUMP.ADTV PMP-1 TURBO.REMOTE_STATUS | 0
1919 | Secunderabad | ADTV PMP-2 POWER_POWER_DISPATCH | ADTV PMP-2 POWER | POWER | TLF | DISPATCH | PUMP.ADTV PMP-2 POWER.ON | 1 | PUMP.ADTV PMP-2 POWER.OFF | 0 | PUMP.ADTV PMP-2 POWER.REMOTE_STATUS | 0
1919 | Secunderabad | ADTV PMP-2 TURBO_TURBO_DISPATCH | ADTV PMP-2 TURBO | TURBO | TLF | DISPATCH | PUMP.ADTV PMP-2 TURBO.ON | 1 | PUMP.ADTV PMP-2 TURBO.OFF | 0 | PUMP.ADTV PMP-2 TURBO.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-01_ETHANOL_DISPATCH | PMP-01 | ETHANOL | TLF | DISPATCH | PUMP.PMP-01.ON | 1 | PUMP.PMP-01.OFF | 0 | PUMP.PMP-01.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-02_ETHANOL_DISPATCH | PMP-02 | ETHANOL | TLF | DISPATCH | PUMP.PMP-02.ON | 1 | PUMP.PMP-02.OFF | 0 | PUMP.PMP-02.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-03_ETHANOL_DISPATCH | PMP-03 | ETHANOL | TLF | DISPATCH | PUMP.PMP-03.ON | 1 | PUMP.PMP-03.OFF | 0 | PUMP.PMP-03.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-05_BIO HSD_DISPATCH | PMP-05 | BIO HSD | TLF | DISPATCH | PUMP.PMP-05.ON | 1 | PUMP.PMP-05.OFF | 0 | PUMP.PMP-05.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-06_BIO HSD_DISPATCH | PMP-06 | BIO HSD | TLF | DISPATCH | PUMP.PMP-06.ON | 1 | PUMP.PMP-06.OFF | 0 | PUMP.PMP-06.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-07_ETHANOL_RECEIPT | PMP-07 | ETHANOL | TWD | RECEIPT | PUMP.PMP-07.ON | 1 | PUMP.PMP-07.OFF | 0 | PUMP.PMP-07.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-08_ETHANOL_RECEIPT | PMP-08 | ETHANOL | TWD | RECEIPT | PUMP.PMP-08.ON | 1 | PUMP.PMP-08.OFF | 0 | PUMP.PMP-08.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-09_ETHANOL_RECEIPT | PMP-09 | ETHANOL | TWD | RECEIPT | PUMP.PMP-09.ON | 1 | PUMP.PMP-09.OFF | 0 | PUMP.PMP-09.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-10_CI_RECEIPT | PMP-10 | CI | TWD | RECEIPT | PUMP.PMP-10.ON | 1 | PUMP.PMP-10.OFF | 0 | PUMP.PMP-10.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-11_CI_RECEIPT | PMP-11 | CI | TWD | RECEIPT | PUMP.PMP-11.ON | 1 | PUMP.PMP-11.OFF | 0 | PUMP.PMP-11.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-47_SKO_RECEIPT | PMP-47 | SKO | TWD | RECEIPT | PUMP.PMP-47.ON | 1 | PUMP.PMP-47.OFF | 0 | PUMP.PMP-47.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-48_SKO_RECEIPT | PMP-48 | SKO | TWD | RECEIPT | PUMP.PMP-48.ON | 1 | PUMP.PMP-48.OFF | 0 | PUMP.PMP-48.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-49_POWER99_RECEIPT | PMP-49 | POWER99 | TWD | RECEIPT | PUMP.PMP-49.ON | 1 | PUMP.PMP-49.OFF | 0 | PUMP.PMP-49.REMOTE_STATUS | 0
1919 | Secunderabad | PMP-50_POWER99_RECEIPT | PMP-50 | POWER99 | TWD | RECEIPT | PUMP.PMP-50.ON | 1 | PUMP.PMP-50.OFF | 0 | PUMP.PMP-50.REMOTE_STATUS | 0
1919 | Secunderabad | VRU-PMP-01_BS IV HSD_RECEIPT | VRU-PMP-01 | BS IV HSD | TWD | RECEIPT | PUMP.VRU-PMP-01.ON | 1 | PUMP.VRU-PMP-01.OFF | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | FIRE PUMP MAINTENANCE Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START 4 | Normal value | FIRE PUMP FAIL TO START 5 | Normal value | FIRE PUMP FAIL TO START STANDBY1 | Normal value | FIRE PUMP FAIL TO START STANDBY2 | Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1919 | Secunderabad | FWP-01_WATER_DISPATCH | FWP-01 | WATER | PH | DISPATCH | PUMP.FWP-01.ON | 1 | PUMP.FWP-01.OFF | 0 | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-02_WATER_DISPATCH | FWP-02 | WATER | PH | DISPATCH | PUMP.FWP-02.ON | 1 | PUMP.FWP-02.OFF | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-03_WATER_DISPATCH | FWP-03 | WATER | PH | DISPATCH | PUMP.FWP-03.ON | 1 | PUMP.FWP-03.OFF | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-03.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-03.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-04_WATER_DISPATCH | FWP-04 | WATER | PH | DISPATCH | PUMP.FWP-04.ON | 1 | PUMP.FWP-04.OFF | 0 | PUMP.FWP-04.REMOTE_STATUS | 0 | PUMP.FWP-04.MAINTENANCE_STATUS | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-04.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-04.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-04.PUMP_TRIPPED | 0 | PUMP.FWP-04.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-05_WATER_DISPATCH | FWP-05 | WATER | PH | DISPATCH | PUMP.FWP-05.ON | 1 | PUMP.FWP-05.OFF | 0 | PUMP.FWP-05.REMOTE_STATUS | 0 | PUMP.FWP-05.MAINTENANCE_STATUS | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-05.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-05.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-05.PUMP_TRIPPED | 0 | PUMP.FWP-05.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-06_WATER_DISPATCH | FWP-06 | WATER | PH | DISPATCH | PUMP.FWP-06.ON | 1 | PUMP.FWP-06.OFF | 0 | PUMP.FWP-06.REMOTE_STATUS | 0 | PUMP.FWP-06.MAINTENANCE_STATUS | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-06.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-06.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-06.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-06.PUMP_TRIPPED | 0 | PUMP.FWP-06.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-07_WATER_DISPATCH | FWP-07 | WATER | PH | DISPATCH | PUMP.FWP-07.ON | 1 | PUMP.FWP-07.OFF | 0 | PUMP.FWP-07.REMOTE_STATUS | 0 | PUMP.FWP-07.MAINTENANCE_STATUS | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN4 | 0 | PUMP.FWP-07.FAILED_TO_START_MAIN5 | 0 | PUMP.FWP-07.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-07.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-07.PUMP_TRIPPED | 0 | PUMP.FWP-07.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | FWP-08_WATER_DISPATCH | FWP-08 | WATER | PH | DISPATCH | PUMP.FWP-08.ON | 1 | PUMP.FWP-08.OFF | 0 | PUMP.FWP-08.REMOTE_STATUS | 0 | PUMP.FWP-08.MAINTENANCE_STATUS | 0 | PUMP.FWP-08.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-08.FAILED_TO_START_MAIN2 |  | PUMP.FWP-08.FAILED_TO_START_MAIN3 |  | PUMP.FWP-08.FAILED_TO_START_MAIN4 |  | PUMP.FWP-08.FAILED_TO_START_MAIN5 |  | PUMP.FWP-08.FAILED_TO_START_STANDBY1 | 0 | PUMP.FWP-08.FAILED_TO_START_STANDBY2 | 0 | PUMP.FWP-08.PUMP_TRIPPED | 0 | PUMP.FWP-08.HIGH_TEMPERATURE_ALARM | 0
1919 | Secunderabad | JCY-01_WATER_DISPATCH | JCY-01 | WATER | PH | DISPATCH | PUMP.JCY-01.ON | 1 | PUMP.JCY-01.OFF | 0 | PUMP.JCY-01.REMOTE_STATUS | 0 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | [9 empty] | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 |  |  | PUMP.JCY-01.PUMP_TRIPPED | 0
1919 | Secunderabad | JCY-02_WATER_DISPATCH | JCY-02 | WATER | PH | DISPATCH | PUMP.JCY-02.ON | 1 | PUMP.JCY-02.OFF | 0 | PUMP.JCY-02.REMOTE_STATUS | 0 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | [9 empty] | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 |  |  | PUMP.JCY-02.PUMP_TRIPPED | 0
1919 | Secunderabad | Hydrant_PT_Farthest Point | Hydrant | PT | Farthest Point | Farthest Point | [6 empty] | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1919 | Secunderabad | Hydrant_PT_Nearest Point | Hydrant | PT | Nearest Point | Nearest Point | [6 empty] | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1919 | Secunderabad | UPS-01_CR | UPS-01 | CR | UPS.UPS-01.MAIN_AC_FAIL | 0 | UPS.UPS-01.LOW_BATTERY | 0 |  |  | UPS.UPS-01.OVERLOAD_ALARM | 0
1919 | Secunderabad | UPS-02_CR | UPS-02 | CR | UPS.UPS-02.MAIN_AC_FAIL | 0 | UPS.UPS-02.LOW_BATTERY | 0 |  |  | UPS.UPS-02.OVERLOAD_ALARM | 0
1919 | Secunderabad | UPS-03_CR | UPS-03 | CR | UPS.UPS-03.MAIN_AC_FAIL | 0 | UPS.UPS-03.LOW_BATTERY | 0 | UPS.UPS-03.LOAD_ON_UPS | 0
1919 | Secunderabad | UPS-04_CR | UPS-04 | CR | UPS.UPS-04.MAIN_AC_FAIL | 0 | UPS.UPS-04.LOW_BATTERY | 0 | UPS.UPS-04.LOAD_ON_UPS | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal value | Sensor_Id | Sensor_Type | PLC B IS MASTER | PLC B IS MASTER Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | PLC A FAIL SAFE Normal Value | Sensor_Id | Sensor_Type | PLC B FAIL SAFE | PLC B FAIL SAFE Normal Value | Sensor_Id | Sensor_Type | PLC A COOMUNCIATION | PLC A COOMUNCIATION Normal Value | Sensor_Id | Sensor_Type | PLC B COOMUNCIATION | PLC B COOMUNCIATION Normal Value | Sensor_Id | Sensor_Type
1919 | Secunderabad | GEPLC_CR | GEPLC | CR | PLC.GEPLC.PLCA_IS_MASTER | 0 | GEPLC | PLC A | PLC.GEPLC.PLCB_IS_MASTER | 1 | GEPLC | PLC B
1919 | Secunderabad | SFT PLC_CR | SFT PLC | CR | PLC.SFTPLC.PLCA_IS_MASTER | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLC B | PLC.SFTPLC.PLCAB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCAB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLC B

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1919 | Secunderabad | HDS-01_OPEN PATH_TANK1A TANK1B | HDS-01 | OPEN PATH | TANK1A TANK1B | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-02_OPEN PATH_TANK1C | HDS-02 | OPEN PATH | TANK1C | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-03_OPEN PATH_PRODUCT PUMP HOUSE | HDS-03 | OPEN PATH | PRODUCT PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-04_OPEN PATH_TANK5C | HDS-04 | OPEN PATH | TANK5C | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-05_POINT TYPE_TANK5A | HDS-05 | POINT TYPE | TANK5A | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-06_POINT TYPE_TANK3C | HDS-06 | POINT TYPE | TANK3C | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-06.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-07_POINT TYPE_TANK4C | HDS-07 | POINT TYPE | TANK4C | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-08_POINT TYPE_TANK1B | HDS-08 | POINT TYPE | TANK1B | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-09_POINT TYPE_TANK1C | HDS-09 | POINT TYPE | TANK1C | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-10_POINT TYPE_TANK 1A | HDS-10 | POINT TYPE | TANK 1A | GDS.HDS-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-10.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-11_POINT TYPE_TANK5B | HDS-11 | POINT TYPE | TANK5B | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-11.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-11.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-12_OPEN PATH_TANK3C | HDS-12 | OPEN PATH | TANK3C | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-12.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-12.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-13_POINT TYPE_TANK4C | HDS-13 | POINT TYPE | TANK4C | GDS.HDS-13.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-13.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-13.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-13.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-13.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-14_HCD-BPCL PLT MFM AREA_BPCL PLT MFM AREA | HDS-14 | HCD-BPCL PLT MFM AREA | BPCL PLT MFM AREA | GDS.HDS-14.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-14.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-14.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-14.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-14.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-15_POINT TYPE_HCD-15 | HDS-15 | POINT TYPE | HCD-15 | GDS.HDS-15.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-15.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-15.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-15.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-15.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-16_POINT TYPE_HCD-16 | HDS-16 | POINT TYPE | HCD-16 | GDS.HDS-16.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-16.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-16.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-16.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-16.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-17_POINT TYPE_HCD-17 | HDS-17 | POINT TYPE | HCD-17 | GDS.HDS-17.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-17.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-17.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-17.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-17.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-18_POINT TYPE_HCD-18 | HDS-18 | POINT TYPE | HCD-18 | GDS.HDS-18.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-18.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-18.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-18.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-18.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HDS-19_POINT TYPE_HCD-19 | HDS-19 | POINT TYPE | HCD-19 | GDS.HDS-19.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-19.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-19.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-19.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-19.MAINTENANCE_CALL | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1919 | Secunderabad | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-05 | DRAINVALVE.DV-05.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-06 | DRAINVALVE.DV-06.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-07 | DRAINVALVE.DV-07.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-08 | DRAINVALVE.DV-08.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-09 | DRAINVALVE.DV-09.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-10 | DRAINVALVE.DV-10.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-11 | DRAINVALVE.DV-11.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-12 | DRAINVALVE.DV-12.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-13 | DRAINVALVE.DV-13.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-14 | DRAINVALVE.DV-14.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-15 | DRAINVALVE.DV-15.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-16 | DRAINVALVE.DV-16.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-17 | DRAINVALVE.DV-17.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-18 | DRAINVALVE.DV-18.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-19 | DRAINVALVE.DV-19.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-20 | DRAINVALVE.DV-20.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-21 | DRAINVALVE.DV-21.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-22 | DRAINVALVE.DV-22.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-23 | DRAINVALVE.DV-23.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-24 | DRAINVALVE.DV-24.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-25 | DRAINVALVE.DV-25.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-26 | DRAINVALVE.DV-26.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-27 | DRAINVALVE.DV-27.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-28 | DRAINVALVE.DV-28.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-29 | DRAINVALVE.DV-29.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-30 | DRAINVALVE.DV-30.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-31 | DRAINVALVE.DV-31.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-32 | DRAINVALVE.DV-32.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-33 | DRAINVALVE.DV-33.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-34 | DRAINVALVE.DV-34.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-35 | DRAINVALVE.DV-35.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | DV-36 | DRAINVALVE.DV-36.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1919 | Secunderabad | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.CLOSE_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1919 | Secunderabad | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.CLOSE_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Hooter Name | Hooter ID | HOOTER STATUS | HOOTER STATUS Normal Value
1919 | Secunderabad | Control room - Dyke/2 FWP/Gantry Permis sive | 1 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1919 | Secunderabad | Control room - ESD | 2 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0
1919 | Secunderabad | Control room - HCD | 3 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_CR | 0
1919 | Secunderabad | HCD activated in Field | 4 | PLC.SFTPLC.EFFECT_HOOTER_FOR_HC_FIELD | 0
1919 | Secunderabad | Dyke activated in field | 5 | PLC.SFTPLC.EFFECT_HOOTER_FOR_RIMSEAL_CR | 0
1919 | Secunderabad | Tank 1A activated in Field | 6 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1919 | Secunderabad | TTL P/H activated in Field | 7 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1919 | Secunderabad | Tank 3C activated in Field | 8 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1919 | Secunderabad | Tank 4C activated in Field | 9 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1919 | Secunderabad | Tank 5A activated in Field | 10 | PLC.SFTPLC.HOOTER_FIELD_5 | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1919 | Secunderabad | ESD-PB-01-Control Room | ESD-01 | ESD-PB-01 | Control Room | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-02-Gantry - 01 | ESD-02 | ESD-PB-02 | Gantry - 01 | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-03-BETWEEN GANTRY 1 AND 2 | ESD-03 | ESD-PB-03 | BETWEEN GANTRY 1 AND 2 | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-04-Gantry - 02 | ESD-04 | ESD-PB-04 | Gantry - 02 | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-05-NEAR TANK-1B | ESD-05 | ESD-PB-05 | NEAR TANK-1B | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-CENTRAL-CENTRAL ESD | ESD-06 | ESD-CENTRAL | CENTRAL ESD | ESD.ESD-06.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-06-WEST OF TK3C | ESD-09 | ESD-PB-06 | WEST OF TK3C | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-07-NEAR TANK-4A | ESD-10 | ESD-PB-07 | NEAR TANK-4A | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-08-NEAR TANK 5B | ESD-11 | ESD-PB-08 | NEAR TANK 5B | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-09-NEAR TANK-1C | ESD-12 | ESD-PB-09 | NEAR TANK-1C | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-13-PIPELINE PLC | ESD-13 | ESD-13 | PIPELINE PLC | ESD.ESD-13.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-10-TLF PPH | ESD-15 | ESD-PB-10 | TLF PPH | ESD.ESD-15.ESD_STATUS | 0 | ESD.ESD-15.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-16-NEAR TANK-3B | ESD-16 | ESD-PB-16 | NEAR TANK-3B | ESD.ESD-16.ESD_STATUS | 0 | ESD.ESD-16.MAINTENANCE_STATUS |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-17-NEAR TANK-5C | ESD-17 | ESD-PB-17 | NEAR TANK-5C | ESD.ESD-17.ESD_STATUS | 0 | ESD.ESD-17.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-18-TLF GANTRY BAY 0 | ESD-18 | ESD-PB-18 | TLF GANTRY BAY 0 | ESD.ESD-18.ESD_STATUS | 0 | ESD.ESD-18.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-19-LIC ROOM | ESD-19 | ESD-PB-19 | LIC ROOM | ESD.ESD-19.ESD_STATUS | 0 | ESD.ESD-19.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-20-SECURITY MAIN GATE | ESD-20 | ESD-PB-20 | SECURITY MAIN GATE | ESD.ESD-20.ESD_STATUS | 0 | ESD.ESD-20.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-21-UNLOADING GANTRY | ESD-21 | ESD-PB-21 | UNLOADING GANTRY | ESD.ESD-21.ESD_STATUS | 0 | ESD.ESD-21.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-22-TLF GANTRY BAY 15 | ESD-22 | ESD-PB-22 | TLF GANTRY BAY 15 | ESD.ESD-22.ESD_STATUS | 0 | ESD.ESD-22.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-PB-24-ESD TO BPCL PH ACB | ESD-24 | ESD-PB-24 | ESD TO BPCL PH ACB | ESD.ESD-24.ESD_STATUS | 0 | ESD.ESD-24.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-BPCL-Common ESD BPCL | ESD-BPCL | ESD-BPCL | Common ESD BPCL | ESD.ESD-BPCL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-IOCL-Common ESD IOCL | ESD-IOCL | ESD-IOCL | Common ESD IOCL | ESD.ESD-IOCL.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0
1919 | Secunderabad | ESD-SOFT-SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.EFFECT_ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.EFFECT_ALL_MOV_CLOSED | 0 |  | 0 | PLC.SFTPLC.EFFECT_SIREN_ACTIVATED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.EFFECT_ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | UNAUTHORISE FLOW STATUS OF BLEND | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF BLEND | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | BCU VS MFM TOTALIZER MISMATCH | BCU VS MFM TOTALIZER MISMATCH Normal Value | DAY START TOTALIZER MISMATCH | DAY START TOTALIZER MISMATCH Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value
1919 | Secunderabad | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Single.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01A.BATCH_STATUS | 0 | SmartLoad-Single.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Single.BC-01A.NOMINAL_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 02_BC-01B_BS VI HSD | LP 02 | TLF | BC-01B | BS VI HSD | SmartLoad-Single.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-01B.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01B.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01B.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01B.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-01B.BATCH_STATUS | 0 | SmartLoad-Single.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-01B.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Single.BC-01B.NOMINAL_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 03_BC-02A_BS VI MS | LP 03 | TLF | BC-02A | BS VI MS | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 04_BC-02B_BS VI HSD | LP 04 | TLF | BC-02B | BS VI HSD | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 05_BC-03A_BS VI MS | LP 05 | TLF | BC-03A | BS VI MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 07_BC-04A_BS VI MS | LP 07 | TLF | BC-04A | BS VI MS | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 09_BC-05A_BS VI MS | LP 09 | TLF | BC-05A | BS VI MS | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 11_BC-06A_BS VI MS | LP 11 | TLF | BC-06A | BS VI MS | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 13_BC-07A_BS VI MS | LP 13 | TLF | BC-07A | BS VI MS | SmartLoad-Dual.BC-07A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-07A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-07A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 14_BC-07B_BS VI HSD | LP 14 | TLF | BC-07B | BS VI HSD | SmartLoad-Dual.BC-07B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-07B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-07B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-07B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-07B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-07B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-07B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 15_BC-09A-LP1_BS VI MS | LP 15 | TLF | BC-09A-LP1 | BS VI MS | SmartLoad-Dual.BC-09A-LP1.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A-LP1.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A-LP1.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A-LP1.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A-LP1.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A-LP1.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A-LP1.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-09A-LP1.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-09A-LP1.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09A-LP1.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A-LP1.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A-LP1.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A-LP1.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 16_BC-09A-LP2_BS VI HSD | LP 16 | TLF | BC-09A-LP2 | BS VI HSD | SmartLoad-Dual.BC-09A-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09A-LP2.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09A-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09A-LP2.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09A-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09A-LP2.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09A-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-09A-LP2.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-09A-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09A-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A-LP2.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-09A-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-09A-LP2.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 17_BC-09B-LP2_SKO | LP 17 | TLF | BC-09B-LP2 | SKO | SmartLoad-Dual.BC-09B-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-09B-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-09B-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 18_BC-0A-LP1_BS VI HSD | LP 18 | TLF | BC-0A-LP1 | BS VI HSD | SmartLoad-Dual.BC-0A-LP1.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-0A-LP1.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-0A-LP1.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-0A-LP1.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-0A-LP1.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-0A-LP1.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-0A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-0A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-0A-LP1.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-0A-LP1.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-0A-LP1.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.BATCH_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-0A-LP1.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-0A-LP1.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-0A-LP1.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-0A-LP1.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 19_BC-0A-LP2_BS VI HSD | LP 19 | TLF | BC-0A-LP2 | BS VI HSD | SmartLoad-Dual.BC-0A-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-0A-LP2.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-0A-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-0A-LP2.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-0A-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-0A-LP2.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-0A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-0A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-0A-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-0A-LP2.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-0A-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-0A-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-0A-LP2.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-0A-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-0A-LP2.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 20_BC-0B-LP1_HEXANE | LP 20 | TLF | BC-0B-LP1 | HEXANE | SmartLoad-Dual.BC-0B-LP1.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.BATCH_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-0B-LP1.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-0B-LP1.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 21_BC-0B-LP2_MTO | LP 21 | TLF | BC-0B-LP2 | MTO | SmartLoad-Dual.BC-0B-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-0B-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-0B-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 22_BC-10A_BS VI MS | LP 22 | TLF | BC-10A | BS VI MS | SmartLoad-Dual.BC-10A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-10A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-10A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 23_BC-10B_BS VI HSD | LP 23 | TLF | BC-10B | BS VI HSD | SmartLoad-Dual.BC-10B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-10B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-10B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-10B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-10B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-10B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-10B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 24_BC-11A_ATF | LP 24 | TLF | BC-11A | ATF | SmartLoad-Dual.BC-11A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-11A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-11A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 25_BC-11B_ATF | LP 25 | TLF | BC-11B | ATF | SmartLoad-Dual.BC-11B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-11B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-11B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-11B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-11B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-11B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 26_BC-12A_ATF | LP 26 | TLF | BC-12A | ATF | SmartLoad-Dual.BC-12A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-12A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-12A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-12A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-12A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-12A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-12A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 27_BC-12B_ATF | LP 27 | TLF | BC-12B | ATF | SmartLoad-Dual.BC-12B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-12B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-12B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-12B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-12B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-12B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 28_BC-13A_BS VI MS | LP 28 | TLF | BC-13A | BS VI MS | SmartLoad-Dual.BC-13A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-13A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-13A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 29_BC-13B_BS VI HSD | LP 29 | TLF | BC-13B | BS VI HSD | SmartLoad-Dual.BC-13B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-13B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-13B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-13B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-13B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-13B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-13B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 30_BC-14A_BS VI MS | LP 30 | TLF | BC-14A | BS VI MS | SmartLoad-Dual.BC-14A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-14A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-14A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 31_BC-14B_BS VI HSD | LP 31 | TLF | BC-14B | BS VI HSD | SmartLoad-Dual.BC-14B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-14B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-14B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-14B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-14B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-14B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-14B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 32_BC-15A_BS VI MS | LP 32 | TLF | BC-15A | BS VI MS | SmartLoad-Dual.BC-15A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-15A.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-15A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 33_BC-15B_BS VI HSD | LP 33 | TLF | BC-15B | BS VI HSD | SmartLoad-Dual.BC-15B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-15B.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-15B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-15B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-15B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-15B.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-15B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-15B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-15B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-15B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15B.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-15B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-15B.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 34_BC-8A-LP1_BS VI HSD | LP 34 | TLF | BC-8A-LP1 | BS VI HSD | SmartLoad-Dual.BC-8A-LP1.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-8A-LP1.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-8A-LP1.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-8A-LP1.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-8A-LP1.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-8A-LP1.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-8A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-8A-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-8A-LP1.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-8A-LP1.METER_OVERRUN_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-8A-LP1.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.BATCH_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-8A-LP1.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-8A-LP1.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-8A-LP1.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-8A-LP1.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 35_BC-8A-LP2_BS VI HSD | LP 35 | TLF | BC-8A-LP2 | BS VI HSD | SmartLoad-Dual.BC-8A-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-8A-LP2.NO_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-8A-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-8A-LP2.LOW_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-8A-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-8A-LP2.HIGH_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-8A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-8A-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-8A-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-8A-LP2.METER_OVERRUN_ALARM_STATUS_M4 | 0 | SmartLoad-Dual.BC-8A-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-8A-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-8A-LP2.BCU_C4_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-8A-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-8A-LP2.NOMINAL_ARM2_COMP2_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 36_BC-8B-LP1_SKO | LP 36 | TLF | BC-8B-LP1 | SKO | SmartLoad-Dual.BC-8B-LP1.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.BATCH_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-8B-LP1.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-8B-LP1.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0
1919 | Secunderabad | LP 37_BC-8B-LP2_SKO | LP 37 | TLF | BC-8B-LP2 | SKO | SmartLoad-Dual.BC-8B-LP2.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.BATCH_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-8B-LP2.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-8B-LP2.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Fire Engine4 | Normal Value | Fire Engine5 | Normal Value | Fire Engine6 | Normal Value | Fire Engine7 | Normal Value | Fire Engine8 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value
1919 | Secunderabad | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.FWP-04.REMOTE_STATUS | 0 | PUMP.FWP-05.REMOTE_STATUS | 0 | PUMP.FWP-06.REMOTE_STATUS | 0 | PUMP.FWP-07.REMOTE_STATUS | 0 | PUMP.FWP-08.REMOTE_STATUS | 0 | PUMP.JCY-01.ON | 1 | PUMP.JCY-02.ON | 1 | PressureTransmitter.PT-01.PRESSURE |  | PressureTransmitter.PT-02.PRESSURE |  | PLC.GEPLC.TOV_ON_SCREEN

## Gantry override
SAPID | Location | Location | OVERRIDE STATUS | OVERRIDE STATUS Normal value
1919 | Secunderabad | Gantry Permissive override condition | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1919 | Secunderabad | Gantry Permissive Write CMD status | SmartLoad-Single.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1919 | Secunderabad | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | TLF Header Line MOV Close | Normal value
1919 | Secunderabad | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0
1919 | Secunderabad | WATER Level below Ref. Volume | PLC.SFTPLC.CAUSE_WATERTK_VOL_BELOW_90PCT | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0
1919 | Secunderabad | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0
1919 | Secunderabad | Gantry Permissive Off |  |  | PLC.SFTPLC.EFFECT_TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.EFFECT_ALL_TLF_PUMP_STOPPED | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | Location ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1919 | Secunderabad | CR LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0