## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Tank Receipt Mode | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1128 | Mathura | TK-01_ETHANOL | TK-01 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | MOV.ROSOV-28.OPEN_STATUS | 0 | ROSOV-28 | ROSOV IL2 | MOV.ROSOV-28.FAILED_TO_CLOSE | 0 | ROSOV-28 | ROSOV FAILED IL2 | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | MOV.ROSOV-29.OPEN_STATUS | 0 | ROSOV-29 | ROSOV RCL | MOV.ROSOV-29.FAILED_TO_CLOSE | 0 | ROSOV-29 | ROSOV FAILED RCL | MOV.DBBV-01.CLOSE_STATUS | 1 | DBBV-01 | MOV IL1 | MOV.DBBV-28.CLOSE_STATUS | 1 | DBBV-28 | MOV IL2 | MOV.DBBV-02.CLOSE_STATUS | 1 | DBBV-02 | MOV OL | MOV.DBBV-31.CLOSE_STATUS | 1 | DBBV-31 | MOV RCL
1128 | Mathura | TK-02_BS VI MS | TK-02 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-02.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar | TANK.TK-02.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED IL1 | MOV.ROSOV-30.OPEN_STATUS | 0 | ROSOV-30 | ROSOV IL2 | MOV.ROSOV-30.FAILED_TO_CLOSE | 0 | ROSOV-30 | ROSOV FAILED IL2 | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED OL | MOV.ROSOV-31.OPEN_STATUS | 0 | ROSOV-31 | ROSOV RCL | MOV.ROSOV-31.FAILED_TO_CLOSE | 0 | ROSOV-31 | ROSOV FAILED RCL | MOV.DBBV-03.CLOSE_STATUS | 1 | DBBV-03 | MOV IL1 | MOV.DBBV-32.CLOSE_STATUS | 1 | DBBV-32 | MOV IL2 | MOV.DBBV-04.CLOSE_STATUS | 1 | DBBV-04 | MOV OL | MOV.DBBV-34.CLOSE_STATUS | 1 | DBBV-34 | MOV RCL
1128 | Mathura | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-03.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar | TANK.TK-03.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED IL1 | MOV.ROSOV-32.OPEN_STATUS | 0 | ROSOV-31 | ROSOV IL2 | MOV.ROSOV-32.FAILED_TO_CLOSE | 0 | ROSOV-31 | ROSOV FAILED IL2 | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED OL | MOV.ROSOV-33.OPEN_STATUS | 0 | ROSOV-33 | ROSOV RCL | MOV.ROSOV-33.FAILED_TO_CLOSE | 0 | ROSOV-33 | ROSOV FAILED RCL | MOV.DBBV-05.CLOSE_STATUS | 1 | DBBV-05 | MOV IL1 | MOV.MOV-001.CLOSE_STATUS | 1 | MOV-001 | MOV IL2 | MOV.DBBV-06.CLOSE_STATUS | 1 | DBBV-06 | MOV OL | MOV.MOV-002.CLOSE_STATUS | 1 | MOV-002 | MOV RCL
1128 | Mathura | TK-04_BS VI HSD | TK-04 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-04.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar | TANK.TK-04.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED IL1 | MOV.ROSOV-34.OPEN_STATUS | 0 | ROSOV-32 | ROSOV IL2 | MOV.ROSOV-34.FAILED_TO_CLOSE | 0 | ROSOV-32 | ROSOV FAILED IL2 | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | MOV.ROSOV-35.OPEN_STATUS | 0 | ROSOV-35 | ROSOV RCL | MOV.ROSOV-35.FAILED_TO_CLOSE | 0 | ROSOV-35 | ROSOV FAILED RCL | MOV.DBBV-07.CLOSE_STATUS | 1 | DBBV-07 | MOV IL1 | MOV.MOV-003.CLOSE_STATUS | 1 | MOV-003 | MOV IL2 | MOV.DBBV-08.CLOSE_STATUS | 1 | DBBV-08 | MOV OL | MOV.MOV-004.CLOSE_STATUS | 1 | MOV-004 | MOV RCL
1128 | Mathura | TK-05_ETHANOL | TK-05 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | MOV.ROSOV-36.OPEN_STATUS | 0 | ROSOV-33 | ROSOV IL2 | MOV.ROSOV-36.FAILED_TO_CLOSE | 0 | ROSOV-33 | ROSOV FAILED IL2 | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED OL | MOV.ROSOV-37.OPEN_STATUS | 0 | ROSOV-37 | ROSOV RCL | MOV.ROSOV-37.FAILED_TO_CLOSE | 0 | ROSOV-37 | ROSOV FAILED RCL | MOV.DBBV-09.CLOSE_STATUS | 1 | DBBV-09 | MOV IL1 | MOV.MOV-005.CLOSE_STATUS | 1 | MOV-005 | MOV IL2 | MOV.DBBV-10.CLOSE_STATUS | 1 | DBBV-10 | MOV OL | MOV.MOV-006.CLOSE_STATUS | 1 | MOV-006 | MOV RCL
1128 | Mathura | TK-06_LDO | TK-06 | AG | LDO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar |  |  | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM | 0 | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar
1128 | Mathura | TK-07_BS VI HSD | TK-07 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-07.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar | TANK.TK-07.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM | 0 | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED IL1 | MOV.ROSOV-38.OPEN_STATUS | 0 | ROSOV-38 | ROSOV IL2 | MOV.ROSOV-38.FAILED_TO_CLOSE | 0 | ROSOV-38 | ROSOV FAILED IL2 | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED OL | MOV.ROSOV-39.OPEN_STATUS | 0 | ROSOV-39 | ROSOV RCL | MOV.ROSOV-39.FAILED_TO_CLOSE | 0 | ROSOV-39 | ROSOV FAILED RCL | MOV.DBBV-11.CLOSE_STATUS | 1 | DBBV-11 | MOV IL1 | MOV.MOV-007.CLOSE_STATUS | 1 | MOV-007 | MOV IL2 | MOV.DBBV-12.CLOSE_STATUS | 1 | DBBV-12 | MOV OL | MOV.MOV-008.CLOSE_STATUS | 1 | MOV-008 | MOV RCL
1128 | Mathura | TK-08_ETHANOL | TK-08 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR
1128 | Mathura | TK-09_BS VI HSD | TK-09 | UG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-09.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar | TANK.TK-09.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1128 | Mathura | TK-10_BS VI MS | TK-10 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-10.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar | TANK.TK-10.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1128 | Mathura | TK-13_WATER | TK-13 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar
1128 | Mathura | TK-14_ETHANOL | TK-14 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar
1128 | Mathura | TK-15_LSHSP | TK-15 | UG | LSHSP | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-15.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar | TANK.TK-15.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar
1128 | Mathura | TK-16_ETHANOL | TK-16 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar |  |  | TANK.TK-16.HIGH_LEVEL | 0 | TK-16 | Primary Radar | TANK.TK-16.TANK_ALERT_ALARM | 0 | TANK.TK-16.HIGH_HIGH_LEVEL | 0 | TK-16 | Primary Radar
1128 | Mathura | TK-17_SKO | TK-17 | AG | SKO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-17.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar | TANK.TK-17.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-17.HIGH_LEVEL | 0 | TK-17 | Primary Radar | TANK.TK-17.TANK_ALERT_ALARM | 0 | TANK.TK-17.HIGH_HIGH_LEVEL | 0 | TK-17 | Primary Radar | [24 empty] | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV IL1 | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-13.CLOSE_STATUS | 1 | DBBV-13 | MOV IL1 |  |  |  |  | MOV.DBBV-14.CLOSE_STATUS | 1 | DBBV-14 | MOV OL
1128 | Mathura | TK-19_BS VI HSD | TK-19 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-19.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-19.LEVEL |  | TK-19 | Primary Radar | TANK.TK-19.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-19.HIGH_LEVEL | 0 | TK-19 | Primary Radar | TANK.TK-19.TANK_ALERT_ALARM | 0 | TANK.TK-19.HIGH_HIGH_LEVEL | 0 | TK-19 | Primary Radar | LEVELSWITCH.LSW-08.SWITCH_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_OK | 0 | LSW-08 | VFT | LEVELSWITCH.LSW-08.PROOF_TEST_FAILED | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.SWITCH_STATUS | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_OK | 0 | RDR-08 | RADAR | LEVELSWITCH.RDR-08.PROOF_TEST_FAILED | 0 | RDR-08 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV OL | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-15.CLOSE_STATUS | 1 | DBBV-15 | MOV IL1 |  |  |  |  | MOV.DBBV-16.CLOSE_STATUS | 1 | DBBV-16 | MOV OL
1128 | Mathura | TK-20_BS VI MS | TK-20 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-20.RECEIPT_PIPELINE_STATUS | 0 |  |  |  |  | TANK.TK-20.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-20.HIGH_LEVEL | 0 | TK-20 | Primary Radar |  | 0 | TANK.TK-20.HIGH_HIGH_LEVEL | 0 | TK-20 | Primary Radar | LEVELSWITCH.LSW-09.SWITCH_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_OK | 0 | LSW-09 | VFT | LEVELSWITCH.LSW-09.PROOF_TEST_FAILED | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.SWITCH_STATUS | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_OK | 0 | RDR-09 | RADAR | LEVELSWITCH.RDR-09.PROOF_TEST_FAILED | 0 | RDR-09 | RADAR | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV IL1 | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV OL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED OL | [8 empty] | MOV.DBBV-17.CLOSE_STATUS | 1 | DBBV-17 | MOV IL1 |  |  |  |  | MOV.DBBV-18.CLOSE_STATUS | 1 | DBBV-18 | MOV OL
1128 | Mathura | TK-21_ETHANOL | TK-21 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-21.LEVEL |  | TK-21 | Primary Radar |  |  | TANK.TK-21.HIGH_LEVEL | 0 | TK-21 | Primary Radar | TANK.TK-21.TANK_ALERT_ALARM | 0 | TANK.TK-21.HIGH_HIGH_LEVEL | 0 | TK-21 | Primary Radar
1128 | Mathura | TK-22_BS VI MS | TK-22 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-22.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-22.LEVEL |  | TK-22 | Primary Radar | TANK.TK-22.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-22.HIGH_LEVEL | 0 | TK-22 | Primary Radar | TANK.TK-22.TANK_ALERT_ALARM | 0 | TANK.TK-22.HIGH_HIGH_LEVEL | 0 | TK-22 | Primary Radar
1128 | Mathura | TK-23_LSHSP | TK-23 | AG | LSHSP | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-23.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-23.LEVEL |  | TK-23 | Primary Radar | TANK.TK-23.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-23.HIGH_LEVEL | 0 | TK-23 | Primary Radar | TANK.TK-23.TANK_ALERT_ALARM | 0 | TANK.TK-23.HIGH_HIGH_LEVEL | 0 | TK-23 | Primary Radar
1128 | Mathura | TK-24_BS VI MS | TK-24 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-24.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-24.LEVEL |  | TK-24 | Primary Radar | TANK.TK-24.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-24.HIGH_LEVEL | 0 | TK-24 | Primary Radar | TANK.TK-24.TANK_ALERT_ALARM | 0 | TANK.TK-24.HIGH_HIGH_LEVEL | 0 | TK-24 | Primary Radar | LEVELSWITCH.LSW-10.SWITCH_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_OK | 0 | LSW-10 | VFT | LEVELSWITCH.LSW-10.PROOF_TEST_FAILED | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.SWITCH_STATUS | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_OK | 0 | RDR-10 | RADAR | LEVELSWITCH.RDR-10.PROOF_TEST_FAILED | 0 | RDR-10 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED RCL | MOV.DBBV-19.CLOSE_STATUS | 1 | DBBV-19 | MOV IL1 |  |  |  |  | MOV.DBBV-20.CLOSE_STATUS | 1 | DBBV-20 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-01.FIRE_ALARM | 0 | RIMSEAL-01 | RIMSEAL | RIMSEAL.RIMSEAL-01.DETECTOR_FAULT | 0 | RIMSEAL-01 | RIMSEAL
1128 | Mathura | TK-25_BS VI MS | TK-25 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-25.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-25.LEVEL |  | TK-25 | Primary Radar | TANK.TK-25.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-25.HIGH_LEVEL | 0 | TK-25 | Primary Radar | TANK.TK-25.TANK_ALERT_ALARM | 0 | TANK.TK-25.HIGH_HIGH_LEVEL | 0 | TK-25 | Primary Radar | LEVELSWITCH.LSW-11.SWITCH_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_OK | 0 | LSW-11 | VFT | LEVELSWITCH.LSW-11.PROOF_TEST_FAILED | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.SWITCH_STATUS | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_OK | 0 | RDR-11 | RADAR | LEVELSWITCH.RDR-11.PROOF_TEST_FAILED | 0 | RDR-11 | RADAR | MOV.ROSOV-22.OPEN_STATUS | 0 | ROSOV-22 | ROSOV IL1 | MOV.ROSOV-22.FAILED_TO_CLOSE | 0 | ROSOV-22 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-23.OPEN_STATUS | 0 | ROSOV-23 | ROSOV OL | MOV.ROSOV-23.FAILED_TO_CLOSE | 0 | ROSOV-23 | ROSOV FAILED OL | MOV.ROSOV-24.OPEN_STATUS | 0 | ROSOV-24 | ROSOV RCL | MOV.ROSOV-24.FAILED_TO_CLOSE | 0 | ROSOV-24 | ROSOV FAILED RCL | MOV.DBBV-22.CLOSE_STATUS | 1 | DBBV-22 | MOV IL1 |  |  |  |  | MOV.DBBV-23.CLOSE_STATUS | 1 | DBBV-23 | MOV OL |  |  |  |  | RIMSEAL.RIMSEAL-02.FIRE_ALARM | 0 | RIMSEAL-02 | RIMSEAL | RIMSEAL.RIMSEAL-02.DETECTOR_FAULT | 0 | RIMSEAL-02 | RIMSEAL
1128 | Mathura | TK-26_SKO | TK-26 | AG | SKO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-26.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-26.LEVEL |  | TK-26 | Primary Radar | TANK.TK-26.RECEIPT_PIPELINE_STATUS | 0 | TANK.TK-26.HIGH_LEVEL | 0 | TK-26 | Primary Radar | TANK.TK-26.TANK_ALERT_ALARM | 0 | TANK.TK-26.HIGH_HIGH_LEVEL | 0 | TK-26 | Primary Radar | LEVELSWITCH.LSW-12.SWITCH_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_OK | 0 | LSW-12 | VFT | LEVELSWITCH.LSW-12.PROOF_TEST_FAILED | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.SWITCH_STATUS | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_OK | 0 | RDR-12 | RADAR | LEVELSWITCH.RDR-12.PROOF_TEST_FAILED | 0 | RDR-12 | RADAR | MOV.ROSOV-25.OPEN_STATUS | 0 | ROSOV-25 | ROSOV IL1 | MOV.ROSOV-25.FAILED_TO_CLOSE | 0 | ROSOV-25 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-26.OPEN_STATUS | 0 | ROSOV-26 | ROSOV OL | MOV.ROSOV-26.FAILED_TO_CLOSE | 0 | ROSOV-26 | ROSOV FAILED OL | MOV.ROSOV-27.OPEN_STATUS | 0 | ROSOV-27 | ROSOV RCL | MOV.ROSOV-27.FAILED_TO_CLOSE | 0 | ROSOV-27 | ROSOV FAILED RCL | MOV.DBBV-25.CLOSE_STATUS | 1 | DBBV-25 | MOV IL1 |  |  |  |  | MOV.DBBV-26.CLOSE_STATUS | 1 | DBBV-26 | MOV OL
1128 | Mathura | TK-29_WATER | TK-29 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-29.LEVEL |  | TK-29 | Primary Radar
1128 | Mathura | TK-30_ETHANOL | TK-30 | UG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-30.LEVEL |  | TK-30 | Primary Radar | [6 empty] | TANK.TK-30.TANK_ALERT_ALARM | 0
1128 | Mathura | TK-31_LDO | TK-31 | AG | LDO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  | TANK.TK-31.LEVEL |  | TK-31 | Primary Radar | [6 empty] | TANK.TK-31.TANK_ALERT_ALARM | 0 | [16 empty] | LEVELSWITCH.RDR-13.SWITCH_STATUS | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_OK | 0 | RDR-13 | RADAR | LEVELSWITCH.RDR-13.PROOF_TEST_FAILED | 0 | RDR-13 | RADAR

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1128 | Mathura_M | TK-01_ETHANOL | TK-01 | AG | ETHANOL | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-28.MAINTENANCE_STATUS | 0 | ROSOV-28 | ROSOV IL2 | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-29.MAINTENANCE_STATUS | 0 | ROSOV-29 | ROSOV RCL | MOV.DBBV-01.MAINTENANCE_STATUS | 0 | DBBV-01 | MOV IL1 | MOV.DBBV-28.MAINTENANCE_STATUS | 0 | DBBV-28 | MOV IL2 | MOV.DBBV-31.MAINTENANCE_STATUS | 0 | DBBV-31 | MOV RCL | MOV.DBBV-02.MAINTENANCE_STATUS | 0 | DBBV-02 | MOV OL
1128 | Mathura_M | TK-02_BS VI MS | TK-02 | AG | BS VI MS | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-30.MAINTENANCE_STATUS | 0 | ROSOV-30 | ROSOV IL2 | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV OL | MOV.ROSOV-31.MAINTENANCE_STATUS | 0 | ROSOV-31 | ROSOV RCL | MOV.DBBV-03.MAINTENANCE_STATUS | 0 | DBBV-03 | MOV IL1 | MOV.DBBV-32.MAINTENANCE_STATUS | 0 | DBBV-32 | MOV IL2 | MOV.DBBV-34.MAINTENANCE_STATUS | 0 | DBBV-34 | MOV RCL | MOV.DBBV-04.MAINTENANCE_STATUS | 0 | DBBV-04 | MOV OL
1128 | Mathura_M | TK-03_BS VI HSD | TK-03 | AG | BS VI HSD | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV IL1 | MOV.ROSOV-32.MAINTENANCE_STATUS | 0 | ROSOV-32 | ROSOV IL2 | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV OL | MOV.ROSOV-33.MAINTENANCE_STATUS | 0 | ROSOV-33 | ROSOV RCL | MOV.DBBV-05.MAINTENANCE_STATUS | 0 | DBBV-05 | MOV IL1 | MOV.MOV-001.MAINTENANCE_STATUS | 0 | MOV-001 | MOV IL2 | MOV.MOV-002.MAINTENANCE_STATUS | 0 | MOV-002 | MOV RCL | MOV.DBBV-06.MAINTENANCE_STATUS | 0 | DBBV-06 | MOV OL
1128 | Mathura_M | TK-04_BS VI HSD | TK-04 | AG | BS VI HSD | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV IL1 | MOV.ROSOV-34.MAINTENANCE_STATUS | 0 | ROSOV-34 | ROSOV IL2 | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-35.MAINTENANCE_STATUS | 0 | ROSOV-35 | ROSOV RCL | MOV.DBBV-07.MAINTENANCE_STATUS | 0 | DBBV-07 | MOV IL1 | MOV.MOV-003.MAINTENANCE_STATUS | 0 | MOV-003 | MOV IL2 | MOV.MOV-004.MAINTENANCE_STATUS | 0 | MOV-004 | MOV RCL | MOV.DBBV-08.MAINTENANCE_STATUS | 0 | DBBV-08 | MOV OL
1128 | Mathura_M | TK-05_ETHANOL | TK-05 | AG | ETHANOL | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-36.MAINTENANCE_STATUS | 0 | ROSOV-36 | ROSOV IL2 | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV OL | MOV.ROSOV-37.MAINTENANCE_STATUS | 0 | ROSOV-37 | ROSOV RCL | MOV.DBBV-09.MAINTENANCE_STATUS | 0 | DBBV-09 | MOV IL1 | MOV.MOV-005.MAINTENANCE_STATUS | 0 | MOV-005 | MOV IL2 | MOV.MOV-006.MAINTENANCE_STATUS | 0 | MOV-006 | MOV RCL | MOV.DBBV-10.MAINTENANCE_STATUS | 0 | DBBV-10 | MOV OL
1128 | Mathura_M | TK-06_LDO | TK-06 | AG | LDO | TANK.TK-06.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-07_BS VI HSD | TK-07 | AG | BS VI HSD | TANK.TK-07.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV IL1 | MOV.ROSOV-38.MAINTENANCE_STATUS | 0 | ROSOV-38 | ROSOV IL2 | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV OL | MOV.ROSOV-39.MAINTENANCE_STATUS | 0 | ROSOV-39 | ROSOV RCL | MOV.DBBV-11.MAINTENANCE_STATUS | 0 | DBBV-11 | MOV IL1 | MOV.MOV-007.MAINTENANCE_STATUS | 0 | MOV-007 | MOV IL2 | MOV.MOV-008.MAINTENANCE_STATUS | 0 | MOV-008 | MOV RCL | MOV.DBBV-12.MAINTENANCE_STATUS | 0 | DBBV-12 | MOV OL
1128 | Mathura_M | TK-08_ETHANOL | TK-08 | UG | ETHANOL | TANK.TK-08.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR
1128 | Mathura_M | TK-09_BS VI HSD | TK-09 | UG | BS VI HSD | TANK.TK-09.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-10_BS VI MS | TK-10 | UG | BS VI MS | TANK.TK-10.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-13_WATER | TK-13 | AG | WATER
1128 | Mathura_M | TK-14_ETHANOL | TK-14 | UG | ETHANOL | TANK.TK-14.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-15_LSHSP | TK-15 | UG | LSHSP | TANK.TK-15.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-16_ETHANOL | TK-16 | UG | ETHANOL | TANK.TK-16.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-17_SKO | TK-17 | AG | SKO | TANK.TK-17.MAINTENANCE_STATUS | 0 | [8 empty] | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL |  |  |  |  | MOV.DBBV-13.MAINTENANCE_STATUS | 0 | DBBV-13 | MOV IL1 | [8 empty] | MOV.DBBV-14.MAINTENANCE_STATUS | 0 | DBBV-14 | MOV OL
1128 | Mathura_M | TK-19_BS VI HSD | TK-19 | AG | BS VI HSD | TANK.TK-19.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-08.MAINTENANCE_STATUS | 0 | LSW-08 | VFT | LEVELSWITCH.RDR-08.MAINTENANCE_STATUS | 0 | RDR-08 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV OL |  |  |  |  | MOV.DBBV-15.MAINTENANCE_STATUS | 0 | DBBV-15 | MOV IL1 | [8 empty] | MOV.DBBV-16.MAINTENANCE_STATUS | 0 | DBBV-16 | MOV OL
1128 | Mathura_M | TK-20_BS VI MS | TK-20 | AG | BS VI MS | TANK.TK-20.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-09.MAINTENANCE_STATUS | 0 | LSW-09 | VFT | LEVELSWITCH.RDR-09.MAINTENANCE_STATUS | 0 | RDR-09 | RADAR | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV OL |  |  |  |  | MOV.DBBV-17.MAINTENANCE_STATUS | 0 | DBBV-17 | MOV IL1 | [8 empty] | MOV.DBBV-18.MAINTENANCE_STATUS | 0 | DBBV-18 | MOV OL
1128 | Mathura_M | TK-21_ETHANOL | TK-21 | UG | ETHANOL | TANK.TK-21.MAINTENANCE_STATUS | 0 | [7 empty] | RADAR
1128 | Mathura_M | TK-22_BS VI MS | TK-22 | UG | BS VI MS | TANK.TK-22.MAINTENANCE_STATUS | 0 | [7 empty] | RADAR
1128 | Mathura_M | TK-23_LSHSP | TK-23 | AG | LSHSP | TANK.TK-23.MAINTENANCE_STATUS | 0 | [7 empty] | RADAR
1128 | Mathura_M | TK-24_BS VI MS | TK-24 | AG | BS VI MS | TANK.TK-24.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-10.MAINTENANCE_STATUS | 0 | LSW-10 | VFT | LEVELSWITCH.RDR-10.MAINTENANCE_STATUS | 0 | RDR-10 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL |  |  |  |  | MOV.DBBV-19.MAINTENANCE_STATUS | 0 | DBBV-19 | MOV IL1 | [8 empty] | MOV.DBBV-20.MAINTENANCE_STATUS | 0 | DBBV-20 | MOV OL
1128 | Mathura_M | TK-25_BS VI MS | TK-25 | AG | BS VI MS | TANK.TK-25.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-11.MAINTENANCE_STATUS | 0 | LSW-11 | VFT | LEVELSWITCH.RDR-11.MAINTENANCE_STATUS | 0 | RDR-11 | RADAR | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-22.MAINTENANCE_STATUS | 0 | ROSOV-22 | ROSOV OL |  |  |  |  | MOV.DBBV-22.MAINTENANCE_STATUS | 0 | DBBV_22 | MOV IL1 | [8 empty] | MOV.DBBV-23.MAINTENANCE_STATUS | 0 | DBBV-23 | MOV OL
1128 | Mathura_M | TK-26_SKO | TK-26 | AG | SKO | TANK.TK-26.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-12.MAINTENANCE_STATUS | 0 | LSW-12 | VFT | LEVELSWITCH.RDR-12.MAINTENANCE_STATUS | 0 | RDR-12 | RADAR | MOV.ROSOV-23.MAINTENANCE_STATUS | 0 | ROSOV-23 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-24.MAINTENANCE_STATUS | 0 | ROSOV-24 | ROSOV OL |  |  |  |  | MOV.DBBV-25.MAINTENANCE_STATUS | 0 | DBBV-25 | MOV IL1 | [8 empty] | MOV.DBBV-26.MAINTENANCE_STATUS | 0 | DBBV-26 | MOV OL
1128 | Mathura_M | TK-29_WATER | TK-29 | AG | WATER | [9 empty] | RADAR
1128 | Mathura_M | TK-30_ETHANOL | TK-30 | UG | ETHANOL | TANK.TK-30.MAINTENANCE_STATUS | 0
1128 | Mathura_M | TK-31_LDO | TK-31 | AG | LDO | TANK.TK-31.MAINTENANCE_STATUS | 0 |  |  |  |  | LEVELSWITCH.RDR-13.MAINTENANCE_STATUS | 0 | RDR-13 | RADAR

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type |  | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value
1128 | Mathura | PMP-01_TURBO_DISPATCH | PMP-01 | TURBO | Additive pumps(remove from logic) | TLF | DISPATCH | PUMP.PMP-01.ON | 1 | PUMP.PMP-01.OFF | 0 | PUMP.PMP-01.REMOTE_STATUS | 0
1128 | Mathura | PMP-02_TURBO_DISPATCH | PMP-02 | TURBO | Additive pumps(remove from logic) | TLF | DISPATCH | PUMP.PMP-02.ON | 1 | PUMP.PMP-02.OFF | 0 | PUMP.PMP-02.REMOTE_STATUS | 0
1128 | Mathura | PMP-03_POWER_DISPATCH | PMP-03 | POWER | Additive pumps(remove from logic) | TLF | DISPATCH | PUMP.PMP-03.ON | 1 | PUMP.PMP-03.OFF | 0 | PUMP.PMP-03.REMOTE_STATUS | 0
1128 | Mathura | PMP-04_POWER_DISPATCH | PMP-04 | POWER | Additive pumps(remove from logic) | TLF | DISPATCH | PUMP.PMP-04.ON | 1 | PUMP.PMP-04.OFF | 0 | PUMP.PMP-04.REMOTE_STATUS | 0
1128 | Mathura | PMP-05_ETHANOL_DISPATCH | PMP-05 | ETHANOL |  | TLF | DISPATCH | PUMP.PMP-05.ON | 1 | PUMP.PMP-05.OFF | 0 | PUMP.PMP-05.REMOTE_STATUS | 0
1128 | Mathura | PMP-06_ETHANOL_DISPATCH | PMP-06 | ETHANOL |  | TLF | DISPATCH | PUMP.PMP-06.ON | 1 | PUMP.PMP-06.OFF | 0 | PUMP.PMP-06.REMOTE_STATUS | 0
1128 | Mathura | PMP-07_ETHANOL_DISPATCH | PMP-07 | ETHANOL |  | TLF | DISPATCH | PUMP.PMP-07.ON | 1 | PUMP.PMP-07.OFF | 0 | PUMP.PMP-07.REMOTE_STATUS | 0
1128 | Mathura | PMP-08_ETHANOL_DISPATCH | PMP-08 | ETHANOL |  | TLF | DISPATCH | PUMP.PMP-08.ON | 1 | PUMP.PMP-08.OFF | 0 | PUMP.PMP-08.REMOTE_STATUS | 0
1128 | Mathura | PMP-09_ETHANOL_DISPATCH | PMP-09 | ETHANOL |  | TLF | DISPATCH | PUMP.PMP-09.ON | 1 | PUMP.PMP-09.OFF | 0 | PUMP.PMP-09.REMOTE_STATUS | 0
1128 | Mathura | PMP-13_SKO_DISPATCH | PMP-13 | SKO |  | TLF | DISPATCH | PUMP.PMP-13.ON | 1 | PUMP.PMP-13.OFF | 0 | PUMP.PMP-13.REMOTE_STATUS | 0
1128 | Mathura | PMP-14_SKO_DISPATCH | PMP-14 | SKO |  | TLF | DISPATCH | PUMP.PMP-14.ON | 1 | PUMP.PMP-14.OFF | 0 | PUMP.PMP-14.REMOTE_STATUS | 0
1128 | Mathura | PMP-15_SKO_DISPATCH | PMP-15 | SKO |  | TLF | DISPATCH | PUMP.PMP-15.ON | 1 | PUMP.PMP-15.OFF | 0 | PUMP.PMP-15.REMOTE_STATUS | 0
1128 | Mathura | PMP-16_FO_DISPATCH | PMP-16 | FO | remove | TLF | DISPATCH | PUMP.PMP-16.ON | 1 | PUMP.PMP-16.OFF | 0 | PUMP.PMP-16.REMOTE_STATUS | 0
1128 | Mathura | PMP-17_FO_DISPATCH | PMP-17 | FO | remove | TLF | DISPATCH | PUMP.PMP-17.ON | 1 | PUMP.PMP-17.OFF | 0 | PUMP.PMP-17.REMOTE_STATUS | 0
1128 | Mathura | PMP-18_BLUE DYE_DISPATCH | PMP-18 | BLUE DYE | remove | TLF | DISPATCH | PUMP.PMP-18.ON | 1 | PUMP.PMP-18.OFF | 0 | PUMP.PMP-18.REMOTE_STATUS | 0
1128 | Mathura | PMP-19_BLUE DYE_DISPATCH | PMP-19 | BLUE DYE | remove | TLF | DISPATCH | PUMP.PMP-19.ON | 1 | PUMP.PMP-19.OFF | 0 | PUMP.PMP-19.REMOTE_STATUS | 0
1128 | Mathura | PMP-20_LDO_DISPATCH | PMP-20 | LDO |  | TLF | DISPATCH | PUMP.PMP-20.ON | 1 | PUMP.PMP-20.OFF | 0 | PUMP.PMP-20.REMOTE_STATUS | 0
1128 | Mathura | PMP-21_LDO_DISPATCH | PMP-21 | LDO |  | TLF | DISPATCH | PUMP.PMP-21.ON | 1 | PUMP.PMP-21.OFF | 0 | PUMP.PMP-21.REMOTE_STATUS | 0
1128 | Mathura | PMP-22_LDO_DISPATCH | PMP-22 | LDO |  | TLF | DISPATCH | PUMP.PMP-22.ON | 1 | PUMP.PMP-22.OFF | 0 | PUMP.PMP-22.REMOTE_STATUS | 0
1128 | Mathura | PMP-23_BS VI HSD_DISPATCH | PMP-23 | BS VI HSD |  | TLF | DISPATCH | PUMP.PMP-23.ON | 1 | PUMP.PMP-23.OFF | 0 | PUMP.PMP-23.REMOTE_STATUS | 0
1128 | Mathura | PMP-24_BS VI HSD_DISPATCH | PMP-24 | BS VI HSD |  | TLF | DISPATCH | PUMP.PMP-24.ON | 1 | PUMP.PMP-24.OFF | 0 | PUMP.PMP-24.REMOTE_STATUS | 0
1128 | Mathura | PMP-25_BS VI HSD_DISPATCH | PMP-25 | BS VI HSD |  | TLF | DISPATCH | PUMP.PMP-25.ON | 1 | PUMP.PMP-25.OFF | 0 | PUMP.PMP-25.REMOTE_STATUS | 0
1128 | Mathura | PMP-26_BS VI HSD_DISPATCH | PMP-26 | BS VI HSD |  | TLF | DISPATCH | PUMP.PMP-26.ON | 1 | PUMP.PMP-26.OFF | 0 | PUMP.PMP-26.REMOTE_STATUS | 0
1128 | Mathura | PMP-27_BS VI HSD_DISPATCH | PMP-27 | BS VI HSD |  | TLF | DISPATCH | PUMP.PMP-27.ON | 1 | PUMP.PMP-27.OFF | 0 | PUMP.PMP-27.REMOTE_STATUS | 0
1128 | Mathura | PMP-28_BS VI MS_DISPATCH | PMP-28 | BS VI MS |  | TLF | DISPATCH | PUMP.PMP-28.ON | 1 | PUMP.PMP-28.OFF | 0 | PUMP.PMP-28.REMOTE_STATUS | 0
1128 | Mathura | PMP-29_BS VI MS_DISPATCH | PMP-29 | BS VI MS |  | TLF | DISPATCH | PUMP.PMP-29.ON | 1 | PUMP.PMP-29.OFF | 0 | PUMP.PMP-29.REMOTE_STATUS | 0
1128 | Mathura | PMP-30_BS VI MS_DISPATCH | PMP-30 | BS VI MS |  | TLF | DISPATCH | PUMP.PMP-30.ON | 1 | PUMP.PMP-30.OFF | 0 | PUMP.PMP-30.REMOTE_STATUS | 0
1128 | Mathura | PMP-31_BS VI MS_DISPATCH | PMP-31 | BS VI MS |  | TLF | DISPATCH | PUMP.PMP-31.ON | 1 | PUMP.PMP-31.OFF | 0 | PUMP.PMP-31.REMOTE_STATUS | 0
1128 | Mathura | PMP-32_BS VI MS_DISPATCH | PMP-32 | BS VI MS |  | TLF | DISPATCH | PUMP.PMP-32.ON | 1 | PUMP.PMP-32.OFF | 0 | PUMP.PMP-32.REMOTE_STATUS | 0
1128 | Mathura | TWP-01_BS VI MS_RECEIPT | TWP-01 | BS VI MS |  | TWD | RECEIPT | PUMP.TWP-01.ON | 1 | PUMP.TWP-01.OFF | 0 | PUMP.TWP-01.REMOTE_STATUS | 0
1128 | Mathura | TWP-02_BS VI MS_RECEIPT | TWP-02 | BS VI MS |  | TWD | RECEIPT | PUMP.TWP-02.ON | 1 | PUMP.TWP-02.OFF | 0 | PUMP.TWP-02.REMOTE_STATUS | 0
1128 | Mathura | TWP-03_BS VI MS_RECEIPT | TWP-03 | BS VI MS |  | TWD | RECEIPT | PUMP.TWP-03.ON | 1 | PUMP.TWP-03.OFF | 0 | PUMP.TWP-03.REMOTE_STATUS | 0
1128 | Mathura | TWP-04_BS VI MS_RECEIPT | TWP-04 | BS VI MS |  | TWD | RECEIPT | PUMP.TWP-04.ON | 1 | PUMP.TWP-04.OFF | 0 | PUMP.TWP-04.REMOTE_STATUS | 0
1128 | Mathura | TWP-05_BS VI HSD_RECEIPT | TWP-05 | BS VI HSD |  | TWD | RECEIPT | PUMP.TWP-05.ON | 1 | PUMP.TWP-05.OFF | 0 | PUMP.TWP-05.REMOTE_STATUS | 0
1128 | Mathura | TWP-06_BS VI HSD_RECEIPT | TWP-06 | BS VI HSD |  | TWD | RECEIPT | PUMP.TWP-06.ON | 1 | PUMP.TWP-06.OFF | 0 | PUMP.TWP-06.REMOTE_STATUS | 0
1128 | Mathura | TWP-07_BS VI HSD_RECEIPT | TWP-07 | BS VI HSD |  | TWD | RECEIPT | PUMP.TWP-07.ON | 1 | PUMP.TWP-07.OFF | 0 | PUMP.TWP-07.REMOTE_STATUS | 0
1128 | Mathura | TWP-08_BS VI HSD_RECEIPT | TWP-08 | BS VI HSD |  | TWD | RECEIPT | PUMP.TWP-08.ON | 1 | PUMP.TWP-08.OFF | 0 | PUMP.TWP-08.REMOTE_STATUS | 0
1128 | Mathura | TWP-09_SKO_RECEIPT | TWP-09 | SKO |  | TWD | RECEIPT | PUMP.TWP-09.ON | 1 | PUMP.TWP-09.OFF | 0 | PUMP.TWP-09.REMOTE_STATUS | 0
1128 | Mathura | TWP-10_SKO_RECEIPT | TWP-10 | SKO |  | TWD | RECEIPT | PUMP.TWP-10.ON | 1 | PUMP.TWP-10.OFF | 0 | PUMP.TWP-10.REMOTE_STATUS | 0
1128 | Mathura | TWP-11_FO_RECEIPT | TWP-11 | FO | remove | TWD | RECEIPT | PUMP.TWP-11.ON | 1 | PUMP.TWP-11.OFF | 0 | PUMP.TWP-11.REMOTE_STATUS | 0
1128 | Mathura | TWP-12_FO_RECEIPT | TWP-12 | FO | remove | TWD | RECEIPT | PUMP.TWP-12.ON | 1 | PUMP.TWP-12.OFF | 0 | PUMP.TWP-12.REMOTE_STATUS | 0
1128 | Mathura | TWP-13_FO_RECEIPT | TWP-13 | FO | remove | TWD | RECEIPT | PUMP.TWP-13.ON | 1 | PUMP.TWP-13.OFF | 0 | PUMP.TWP-13.REMOTE_STATUS | 0
1128 | Mathura | TWP-14_FO_RECEIPT | TWP-14 | FO | remove | TWD | RECEIPT | PUMP.TWP-14.ON | 1 | PUMP.TWP-14.OFF | 0 | PUMP.TWP-14.REMOTE_STATUS | 0
1128 | Mathura | TWP-15_LDO_RECEIPT | TWP-15 | LDO |  | TWD | RECEIPT | PUMP.TWP-15.ON | 1 | PUMP.TWP-15.OFF | 0 | PUMP.TWP-15.REMOTE_STATUS | 0
1128 | Mathura | TWP-16_LDO_RECEIPT | TWP-16 | LDO |  | TWD | RECEIPT | PUMP.TWP-16.ON | 1 | PUMP.TWP-16.OFF | 0 | PUMP.TWP-16.REMOTE_STATUS | 0
1128 | Mathura | VRU-PMP-01_BS VI HSD_ | VRU-PMP-01 | BS VI HSD |  | VRU |  | PUMP.VRU-PMP-01.ON | 1 | PUMP.VRU-PMP-01.OFF | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | FIRE PUMP MAINTENANCE Normal value | TANK WATER LEVEL LOW | TANK WATER LEVEL LOW Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | FIRE PUMP FAIL TO START STANDBY Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1128 | Mathura | FWP-01_WATER_DISPATCH | FWP-01 | WATER | PH | DISPATCH | PUMP.FWP-01.ON | 1 | PUMP.FWP-01.OFF | 0 | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 | PUMP.FWP-01.LOW_LUBE_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1128 | Mathura | FWP-02_WATER_DISPATCH | FWP-02 | WATER | PH | DISPATCH | PUMP.FWP-02.ON | 1 | PUMP.FWP-02.OFF | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 | PUMP.FWP-02.LOW_LUBE_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1128 | Mathura | FWP-03_WATER_DISPATCH | FWP-03 | WATER | PH | DISPATCH | PUMP.FWP-03.ON | 1 | PUMP.FWP-03.OFF | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-03.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 | PUMP.FWP-03.LOW_LUBE_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1128 | Mathura | FWP-04_WATER_DISPATCH | FWP-04 | WATER | PH | DISPATCH | PUMP.FWP-04.ON | 1 | PUMP.FWP-04.OFF | 0 | PUMP.FWP-04.REMOTE_STATUS | 0 | PUMP.FWP-04.MAINTENANCE_STATUS | 0 |  |  | PUMP.FWP-04.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-04.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-04.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-04.PUMP_TRIPPED | 0 | PUMP.FWP-04.LOW_LUBE_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-04.HIGH_TEMPERATURE_ALARM | 0
1128 | Mathura | FWP-05_WATER_DISPATCH | FWP-05 | WATER | PH | DISPATCH | PUMP.FWP-05.ON | 1 | PUMP.FWP-05.OFF | 0 | PUMP.FWP-05.REMOTE_STATUS | 0 | PUMP.FWP-05.MAINTENANCE_STATUS | 0 |  |  | PUMP.FWP-05.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN2 | 0 | PUMP.FWP-05.FAILED_TO_START_MAIN3 | 0 | PUMP.FWP-05.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-05.PUMP_TRIPPED | 0 | PUMP.FWP-05.LOW_LUBE_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-05.HIGH_TEMPERATURE_ALARM | 0
1128 | Mathura | JCY-01_WATER_DISPATCH | JCY-01 | WATER | PH | DISPATCH | PUMP.JCY-01.ON | 1 | PUMP.JCY-01.OFF | 0 | PUMP.JCY-01.REMOTE_STATUS | 0 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 |  |  | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-01.PUMP_TRIPPED | 0
1128 | Mathura | JCY-02_WATER_DISPATCH | JCY-02 | WATER | PH | DISPATCH | PUMP.JCY-02.ON | 1 | PUMP.JCY-02.OFF | 0 | PUMP.JCY-02.REMOTE_STATUS | 0 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 |  |  | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-02.PUMP_TRIPPED | 0
1128 | Mathura | Farthest Point PT_WATER Pressure_Near Tank no. 01 | Farthest Point PT | WATER Pressure | PT | Near Tank no. 01 | [6 empty] | PressureTransmitter.PT-08.MAINTENANCE_STATUS | 0
1128 | Mathura | Nearest Point PT_WATER Pressure_FWP pump house | Nearest Point PT | WATER Pressure | PT | FWP pump house | [6 empty] | PressureTransmitter.PT-09.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1128 | Mathura | UPS-01_CR - Process | UPS-01 | CR - Process | UPS.UPS-01.UPS_FAIL | 0
1128 | Mathura | UPS-02_CR - Process | UPS-02 | CR - Process | UPS.UPS-02.UPS_FAIL | 0
1128 | Mathura | UPS-03_CR - Safety | UPS-03 | CR - Safety |  |  | UPS.UPS-03.LOW_BATTERY | 0 | UPS.UPS-03.UPS_ON | 0 | UPS.UPS-03.MAIN_AC_FAIL | 0
1128 | Mathura | UPS-04_CR - Safety | UPS-04 | CR - Safety |  |  | UPS.UPS-04.LOW_BATTERY | 0 | UPS.UPS-04.UPS_ON | 0 | UPS.UPS-04.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | PLC A IS MASTER Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | PLC B IS MASTER Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | PLC A FAIL SAFE Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | PLC B FAIL SAFE Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | PLC A COOMUNCIATION Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | PLC B COOMUNCIATION Normal Value | Sensor_Id | Sensor_Type
1128 | Mathura | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLC A | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLC B
1128 | Mathura | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLC B

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1128 | Mathura | HDS-01_OPEN TYPE_NEW TWD PUMP HOUSE | HDS-01 | OPEN TYPE | NEW TWD PUMP HOUSE | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-02_OPEN TYPE_OLD TWD PUMP HOUSE | HDS-02 | OPEN TYPE | OLD TWD PUMP HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-03_OPEN TYPE_NEAR TANK - 01 | HDS-03 | OPEN TYPE | NEAR TANK - 01 | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-04_POINT TYPE_NEAR TANK - 01 | HDS-04 | POINT TYPE | NEAR TANK - 01 | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | HDS-05_OPEN TYPE_NEAR TANK - 24 | HDS-05 | OPEN TYPE | NEAR TANK - 24 | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-06_OPEN TYPE_NEAR TANK -25 | HDS-06 | OPEN TYPE | NEAR TANK -25 | GDS.HDS-06.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-06.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-06.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-06.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-06.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-07_OPEN TYPE_TLF PUMP HOUSE | HDS-07 | OPEN TYPE | TLF PUMP HOUSE | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-08_POINT TYPE_NEAR TANK -07 | HDS-08 | POINT TYPE | NEAR TANK -07 | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | HDS-09_OPEN PATH_NEAR TANK - 20 | HDS-09 | OPEN PATH | NEAR TANK - 20 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-10_POINT TYPE_NEAR TANK - 23 | HDS-10 | POINT TYPE | NEAR TANK - 23 | GDS.HDS-10.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-10.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-10.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-10.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-10.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | HDS-11_OPEN PATH_NEAR UG PUMP HOUSE | HDS-11 | OPEN PATH | NEAR UG PUMP HOUSE | GDS.HDS-11.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-11.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-11.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-11.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-11.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-12_OPEN PATH_NEAR TK-5 | HDS-12 | OPEN PATH | NEAR TK-5 | GDS.HDS-12.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-12.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-12.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-12.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-12.MAINTENANCE_CALL | 0
1128 | Mathura | HDS-13_POINT TYPE_NEW TWD PH SUM | HDS-13 | POINT TYPE | NEW TWD PH SUM | GDS.HDS-13.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-13.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-13.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-13.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-13.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | HDS-14_POINT TYPE_TLF PH SUM | HDS-14 | POINT TYPE | TLF PH SUM | GDS.HDS-14.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-14.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-14.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-14.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-14.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | HDS-15_POINT TYPE_OLD TWD PH SUM | HDS-15 | POINT TYPE | OLD TWD PH SUM | GDS.HDS-15.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-15.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-15.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-15.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-15.MAINTENANCE_CALL | 0 | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1128 | Mathura | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1128 | Mathura | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1128 | Mathura | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1128 | Mathura | DV-04 | DRAINVALVE.DV-04.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1128 | Mathura | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.CLOSE_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1128 | Mathura | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.CLOSE_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1128 | Mathura | Hooter1_ANY_HOOTER_FOR_HCD_FIELD | Hooter1 | ANY_HOOTER_FOR_HCD_FIELD | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1128 | Mathura | Hooter2_HOOTER_ACK | Hooter2 | HOOTER_ACK | PLC.SFTPLC.HOOTER_ACK | 0
1128 | Mathura | Hooter3_HOOTER_ACK_STATUS | Hooter3 | HOOTER_ACK_STATUS | PLC.SFTPLC.HOOTER_ACK_STATUS | 0
1128 | Mathura | Hooter4_HOOTER_FIELD_1 | Hooter4 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1128 | Mathura | Hooter5_HOOTER_FIELD_2 | Hooter5 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1128 | Mathura | Hooter6_HOOTER_FIELD_3 | Hooter6 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1128 | Mathura | Hooter7_HOOTER_FIELD_4 | Hooter7 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0
1128 | Mathura | Hooter8_HOOTER_FOR_ESD_CR | Hooter8 | HOOTER_FOR_ESD_CR | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1128 | Mathura | Hooter9_HOOTER_FOR_HC_CR | Hooter9 | HOOTER_FOR_HC_CR | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1128 | Mathura | Hooter10_HOOTER_FOR_RIMSEAL_CR | Hooter10 | HOOTER_FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1128 | Mathura | Hooter11_HOOTER_RESET | Hooter11 | HOOTER_RESET | PLC.SFTPLC.HOOTER_RESET | 0
1128 | Mathura | Hooter12_HOOTER_RESET_STATUS | Hooter12 | HOOTER_RESET_STATUS | PLC.SFTPLC.HOOTER_RESET_STATUS | 0
1128 | Mathura | Hooter13_HOOTER_STATUS | Hooter13 | HOOTER_STATUS | PLC.SFTPLC.HOOTER_STATUS | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1128 | Mathura | ESD-01_OUTSIDE S AND D BUILDING | ESD-01 | ESD-PB-01 | OUTSIDE S AND D BUILDING | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-02_OUTSIDE CONTROL ROOM and LIC ROOM | ESD-02 | ESD-PB-02 AND 03 | OUTSIDE CONTROL ROOM and LIC ROOM | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-03_TLF GANTRY BAY NO 12 AND 13 | ESD-03 | ESD-PB-07 | TLF GANTRY BAY NO 12 AND 13 | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-04_NOT USED6 | ESD-04 | NOT USED6 | NOT USED6 | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-05_MCC ROOM | ESD-05 | ESD-PB-05 | MCC ROOM | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-08_TLF PUMP HOUSE | ESD-08 | ESD-PB-06 | TLF PUMP HOUSE | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-09_TLF GANTRY BAY NO 4 AND 5 | ESD-09 | ESD-PB-04 | TLF GANTRY BAY NO 4 AND 5 | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-10_NEAR TANK - 01 | ESD-10 | ESD-PB-08 | NEAR TANK - 01 | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-11_FRONT OF TK-03 | ESD-11 | ESD-PB-09 | FRONT OF TK-03 | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-12_BEHIND TK-03 | ESD-12 | ESD-PB-10 | BEHIND TK-03 | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-13_TWD PUMP HOUSE | ESD-13 | ESD-PB-11 | TWD PUMP HOUSE | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-16_CENTRAL ESD | ESD-16 | ESD-CENTRAL | CENTRAL ESD | ESD.ESD-16.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-19_ESD FROM PIPELINE | ESD-19 | ESD-PIPELINE | ESD FROM PIPELINE | ESD.ESD-19.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-25_IN FRONT OF TK-25 | ESD-25 | ESD-PB-15 | IN FRONT OF TK-25 | ESD.ESD-25.ESD_STATUS | 0 | ESD.ESD-25.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-26_IN FRONT OF TK-24 | ESD-26 | ESD-PB-16 | IN FRONT OF TK-24 | ESD.ESD-26.ESD_STATUS | 0 | ESD.ESD-26.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-27_TWD RAILWAY SIDING | ESD-27 | ESD-PB-12/13 | TWD RAILWAY SIDING | ESD.ESD-27.ESD_STATUS | 0 | ESD.ESD-27.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-28_TWD RAILWAY SIDING IBP GATE | ESD-28 | ESD-PB-14 | TWD RAILWAY SIDING IBP GATE | ESD.ESD-28.ESD_STATUS | 0 | ESD.ESD-28.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1128 | Mathura | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | BCU VS MFM TOTALIZER MISMATCH Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1128 | Mathura | LP 01_BC-501A_BS VI MS | LP 01 | TLF | BC-501A | BS VI MS | SmartLoad-Dual.BC-501A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-501A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-501A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501A.BATCH_STATUS |  | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-501A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-501A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 02_BC-501B_BS VI HSD | LP 02 | TLF | BC-501B | BS VI HSD | SmartLoad-Dual.BC-501B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-501B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-501B.BATCH_STATUS |  | SmartLoad-Dual.BC-501B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-501B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 03_BC-502A_BS VI MS | LP 03 | TLF | BC-502A | BS VI MS | SmartLoad-Dual.BC-502A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-502A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-502A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502A.BATCH_STATUS |  | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-502A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-502A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 04_BC-502B_BS VI HSD | LP 04 | TLF | BC-502B | BS VI HSD | SmartLoad-Dual.BC-502B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-502B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-502B.BATCH_STATUS |  | SmartLoad-Dual.BC-502B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-502B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 05_BC-503A_BS VI MS | LP 05 | TLF | BC-503A | BS VI MS | SmartLoad-Dual.BC-503A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-503A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-503A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503A.BATCH_STATUS |  | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-503A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-503A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 06_BC-503B_BS VI HSD | LP 06 | TLF | BC-503B | BS VI HSD | SmartLoad-Dual.BC-503B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-503B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-503B.BATCH_STATUS |  | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-503B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 07_BC-504A_BS VI MS | LP 07 | TLF | BC-504A | BS VI MS | SmartLoad-Dual.BC-504A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-504A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-504A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504A.BATCH_STATUS |  | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-504A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-504A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 08_BC-504B_BS VI HSD | LP 08 | TLF | BC-504B | BS VI HSD | SmartLoad-Dual.BC-504B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-504B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-504B.BATCH_STATUS |  | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-504B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 09_BC-505A_BS VI MS | LP 09 | TLF | BC-505A | BS VI MS | SmartLoad-Dual.BC-505A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-505A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-505A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505A.BATCH_STATUS |  | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 10_BC-505B_BS VI HSD | LP 10 | TLF | BC-505B | BS VI HSD | SmartLoad-Dual.BC-505B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-505B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-505B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-505B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-505B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-505B.BATCH_STATUS |  | SmartLoad-Dual.BC-505B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-505B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 11_BC-506A_BS VI MS | LP 11 | TLF | BC-506A | BS VI MS | SmartLoad-Dual.BC-506A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-506A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-506A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-506A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-506A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506A.BATCH_STATUS |  | SmartLoad-Dual.BC-506A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-506A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 12_BC-506B_BS VI HSD | LP 12 | TLF | BC-506B | BS VI HSD | SmartLoad-Dual.BC-506B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-506B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-506B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-506B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-506B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-506B.BATCH_STATUS |  | SmartLoad-Dual.BC-506B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-506B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-506B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 13_BC-507A_BS VI MS | LP 13 | TLF | BC-507A | BS VI MS | SmartLoad-Dual.BC-507A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-507A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-507A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-507A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-507A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507A.BATCH_STATUS |  | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-507A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-507A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 14_BC-507B_BS VI HSD | LP 14 | TLF | BC-507B | BS VI HSD | SmartLoad-Dual.BC-507B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-507B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-507B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-507B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-507B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-507B.BATCH_STATUS |  | SmartLoad-Dual.BC-507B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-507B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-507B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 15_BC-508A_BS VI MS | LP 15 | TLF | BC-508A | BS VI MS | SmartLoad-Dual.BC-508A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-508A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-508A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-508A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-508A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508A.BATCH_STATUS |  | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-508A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-508A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-508A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 16_BC-508B_BS VI HSD | LP 16 | TLF | BC-508B | BS VI HSD | SmartLoad-Dual.BC-508B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-508B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-508B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-508B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-508B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-508B.BATCH_STATUS |  | SmartLoad-Dual.BC-508B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-508B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-508B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 17_BC-509A_BS VI MS | LP 17 | TLF | BC-509A | BS VI MS | SmartLoad-Dual.BC-509A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-509A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-509A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-509A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-509A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-509A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-509A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509A.BATCH_STATUS |  | SmartLoad-Dual.BC-509A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-509A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-509A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-509A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-509A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 18_BC-509B_BS VI HSD | LP 18 | TLF | BC-509B | BS VI HSD | SmartLoad-Dual.BC-509B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-509B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-509B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-509B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-509B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-509B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-509B.BATCH_STATUS |  | SmartLoad-Dual.BC-509B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-509B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-509B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 19_BC-510A_BS VI MS | LP 19 | TLF | BC-510A | BS VI MS | SmartLoad-Dual.BC-510A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.HIGH_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-510A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-510A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-510A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-510A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510A.BATCH_STATUS |  | SmartLoad-Dual.BC-510A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-510A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-510A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-510A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-510A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 20_BC-510B_BS VI HSD | LP 20 | TLF | BC-510B | BS VI HSD | SmartLoad-Dual.BC-510B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-510B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-510B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-510B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-510B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-510B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-510B.BATCH_STATUS |  | SmartLoad-Dual.BC-510B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-510B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-510B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 21_BC-511A_BS VI HSD | LP 21 | TLF | BC-511A | BS VI HSD | SmartLoad-Dual.BC-511A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-511A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-511A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-511A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-511A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-511A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-511A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-511A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511A.BATCH_STATUS |  | SmartLoad-Dual.BC-511A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-511A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-511A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 22_BC-511B_BS VI HSD | LP 22 | TLF | BC-511B | BS VI HSD | SmartLoad-Dual.BC-511B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-511B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-511B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-511B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-511B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-511B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-511B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Dual.BC-511B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-511B.BATCH_STATUS |  | SmartLoad-Dual.BC-511B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-511B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-511B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 23_BC-512A_LSHSP | LP 23 | TLF | BC-512A | LSHSP | SmartLoad-Single.BC-512A.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-512A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-512A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-512A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-512A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-512A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-512A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-512A.BATCH_STATUS |  | SmartLoad-Single.BC-512A.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-512A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-512A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 24_BC-512B_SKO | LP 24 | TLF | BC-512B | SKO | SmartLoad-Single.BC-512B.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-512B.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512B.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512B.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-512B.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-512B.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-512B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-512B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-512B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-512B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-512B.BATCH_STATUS |  | SmartLoad-Single.BC-512B.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-512B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-512B.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 25_BC-513A_LSHSP | LP 25 | TLF | BC-513A | LSHSP | SmartLoad-Single.BC-513A.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-513A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-513A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-513A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-513A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-513A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-513A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-513A.BATCH_STATUS |  | SmartLoad-Single.BC-513A.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-513A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-513A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 26_BC-513B_LDO | LP 26 | TLF | BC-513B | LDO | SmartLoad-Single.BC-513B.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-513B.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513B.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513B.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-513B.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-513B.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-513B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-513B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-513B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-513B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-513B.BATCH_STATUS |  | SmartLoad-Single.BC-513B.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-513B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-513B.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 27_BC-514A_LSHSP | LP 27 | TLF | BC-514A | LSHSP | SmartLoad-Single.BC-514A.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-514A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-514A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-514A.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-514A.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-514A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-514A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-514A.BATCH_STATUS |  | SmartLoad-Single.BC-514A.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-514A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-514A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1128 | Mathura | LP 28_BC-514B_LDO | LP 28 | TLF | BC-514B | LDO | SmartLoad-Single.BC-514B.EARTH_ALARM_STATUS | 0 | SmartLoad-Single.BC-514B.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514B.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514B.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Single.BC-514B.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-514B.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Single.BC-514B.BLEND_UNDERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-514B.ADDITIVE_OVERDOSE_ALARM_STATUS | 1 | SmartLoad-Single.BC-514B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-514B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Single.BC-514B.BATCH_STATUS |  | SmartLoad-Single.BC-514B.NOMINAL_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Single.BC-514B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Single.BC-514B.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1128 | Mathura | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1128 | Mathura | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-501A.PERMISSIVE_FROM_DNC_STATUS | 0
1128 | Mathura | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | TLF Header Line MOV Close | TLF Header Line MOV Close Normal value | Hooter activated in control room | Normal value
1128 | Mathura | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1128 | Mathura | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1128 | Mathura | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1128 | Mathura | Gantry Permissive Off |  |  | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1128 | Mathura | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Fire Engine4 | Normal Value | Fire Engine5 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1128 | Mathura | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.FWP-04.REMOTE_STATUS | 0 | PUMP.FWP-05.REMOTE_STATUS | 0 | PUMP.JCY-01.ON | 1 | PUMP.JCY-02.ON | 1 | PressureTransmitter.PT-08.MAINTENANCE_STATUS |  | PressureTransmitter.PT-09.MAINTENANCE_STATUS |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAIN_FWP_AVAIL_REMOTE |  | PUMP.JCY-01.REMOTE_STATUS | 1 |  | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 |  | 1