## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Sensor_Id | Sensor_type | Tank Receipt Mode | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | TANK LEAKAGE STATUS | TANK LEAKAGE STATUS Normal value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Primary Gauge HIGH HIGH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | LEVEL SWITCH Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | LEVEL SWITCH PROOF OK Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | LEVEL SWITCH PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | RADAR HHH Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | RADAR PROOF Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | RADAR PROOF FAILED Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | ROSOV FAIL TO CLOSE STATUS IL2 Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | ROSOV OPEN STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | ROSOV FAIL TO CLOSE STATUS OL Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1155 | Roorkee | TK-01_BS VI MS | TK-01 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.TANK_ALERT_ALARM | 0 | TK-01 | Primary Radar | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar
1155 | Roorkee | TK-02_BS VI MS | TK-02 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.TANK_ALERT_ALARM |  | TK-02 | Primary Radar | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar
1155 | Roorkee | TK-03_ETHANOL | TK-03 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.TANK_ALERT_ALARM |  | TK-03 | Primary Radar | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar
1155 | Roorkee | TK-04_ETHANOL | TK-04 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.TANK_ALERT_ALARM |  | TK-04 | Primary Radar | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar
1155 | Roorkee | TK-05_BIO DIESEL | TK-05 |  | BIO DIESEL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.TANK_ALERT_ALARM |  | TK-05 | Primary Radar | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar
1155 | Roorkee | TK-06_ETHANOL | TK-06 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-06.LEVEL |  | TK-06 | Primary Radar | TANK.TK-06.HIGH_LEVEL | 0 | TK-06 | Primary Radar | TANK.TK-06.TANK_ALERT_ALARM |  | TK-06 | Primary Radar | TANK.TK-06.HIGH_HIGH_LEVEL | 0 | TK-06 | Primary Radar
1155 | Roorkee | TK-07_SKO | TK-07 |  | SKO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar | TANK.TK-07.HIGH_LEVEL | 0 | TK-07 | Primary Radar | TANK.TK-07.TANK_ALERT_ALARM |  | TK-07 | Primary Radar | TANK.TK-07.HIGH_HIGH_LEVEL | 0 | TK-07 | Primary Radar
1155 | Roorkee | TK-08_ETHANOL | TK-08 |  | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.TANK_ALERT_ALARM |  | TK-08 | Primary Radar | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV IL1 | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL1 | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL1 | [8 empty] | MOV.DBBV-001.OPEN_STATUS | 1 | DBBV-001 | MOV IL1 |  |  |  |  | MOV.DBBV-003.OPEN_STATUS | 1 | DBBV-003 | MOV OL
1155 | Roorkee | TK-09_BS VI HSD | TK-09 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.TANK_ALERT_ALARM |  | TK-09 | Primary Radar | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV IL1 | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV OL1 | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED OL1 | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV RCL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV RCL | MOV.DBBV-004.OPEN_STATUS | 1 | DBBV-004 | MOV IL1 |  |  |  |  | MOV.DBBV-005.OPEN_STATUS | 1 | DBBV-005 | MOV OL | MOV.DBBV-006.OPEN_STATUS | 1 | DBBV-006 | MOV RCL
1155 | Roorkee | TK-10_BS VI HSD | TK-10 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.TANK_ALERT_ALARM |  | TK-10 | Primary Radar | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL1 | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL1 | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV RCL | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV RCL | MOV.DBBV-007.OPEN_STATUS | 1 | DBBV-007 | MOV IL1 |  |  |  |  | MOV.DBBV-008.OPEN_STATUS | 1 | DBBV-008 | MOV OL | MOV.DBBV-009.OPEN_STATUS | 1 | DBBV-009 | MOV RCL
1155 | Roorkee | TK-11_BS VI MS | TK-11 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.TANK_ALERT_ALARM |  | TK-11 | Primary Radar | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV IL1 | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV OL1 | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED OL1 | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV RCL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV RCL | MOV.DBBV-010.OPEN_STATUS | 1 | DBBV-010 | MOV IL1 |  |  |  |  | MOV.DBBV-011.OPEN_STATUS | 1 | DBBV-011 | MOV OL | MOV.DBBV-012.OPEN_STATUS | 1 | DBBV-012 | MOV RCL
1155 | Roorkee | TK-12_BS VI MS | TK-12 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.TANK_ALERT_ALARM |  | TK-12 | Primary Radar | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV OL1 | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED OL1 | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV RCL | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV RCL | MOV.DBBV-013.OPEN_STATUS | 1 | DBBV-013 | MOV IL1 |  |  |  |  | MOV.DBBV-014.OPEN_STATUS | 1 | DBBV-014 | MOV OL | MOV.DBBV-015.OPEN_STATUS | 1 | DBBV-015 | MOV RCL
1155 | Roorkee | TK-13_WATER | TK-13 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  |  |  | TANK.TK-13.TANK_ALERT_ALARM |  | TK-13 | Primary Radar
1155 | Roorkee | TK-14_WATER | TK-14 |  | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  |  |  | TANK.TK-14.TANK_ALERT_ALARM |  | TK-14 | Primary Radar
1155 | Roorkee | TK-15_BS VI MS | TK-15 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.TANK_ALERT_ALARM |  | TK-15 | Primary Radar | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar
1155 | Roorkee | TK-16_BS VI MS | TK-16 |  | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-16.LEVEL |  | TK-16 | Primary Radar | TANK.TK-16.HIGH_LEVEL | 0 | TK-16 | Primary Radar | TANK.TK-16.TANK_ALERT_ALARM |  | TK-16 | Primary Radar | TANK.TK-16.HIGH_HIGH_LEVEL | 0 | TK-16 | Primary Radar
1155 | Roorkee | TK-17_BS VI HSD | TK-17 |  | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 |  |  |  |  | TANK.TK-17.LEVEL |  | TK-17 | Primary Radar | TANK.TK-17.HIGH_LEVEL | 0 | TK-17 | Primary Radar | TANK.TK-17.TANK_ALERT_ALARM |  | TK-17 | Primary Radar | TANK.TK-17.HIGH_HIGH_LEVEL | 0 | TK-17 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV IL1 | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV OL1 | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED OL1 | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV RCL | MOV.DBBV-018.OPEN_STATUS | 1 | DBBV-018 | MOV IL1 |  |  |  |  | MOV.DBBV-019.OPEN_STATUS | 1 | DBBV-019 | MOV OL | MOV.DBBV-020.OPEN_STATUS | 1 | DBBV-020 | MOV RCL

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1155 | Roorkee_M | TK-01_BS VI MS | TK-01 |  | BS VI MS | TANK.TK-01.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-02_BS VI MS | TK-02 |  | BS VI MS | TANK.TK-02.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-03_ETHANOL | TK-03 |  | ETHANOL | TANK.TK-03.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-04_ETHANOL | TK-04 |  | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-05_BIO DIESEL | TK-05 |  | BIO DIESEL | TANK.TK-05.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-06_ETHANOL | TK-06 |  | ETHANOL | TANK.TK-06.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-07_SKO | TK-07 |  | SKO | TANK.TK-07.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-08_ETHANOL | TK-08 |  | ETHANOL | TANK.TK-08.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VTF | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL |  |  |  |  | MOV.DBBV-001.MAINTENANCE_STATUS | 0 | DBBV-001 | MOV IL1 | [8 empty] | MOV.DBBV-003.MAINTENANCE_STATUS | 0 | DBBV-003 | MOV OL
1155 | Roorkee_M | TK-09_BS VI HSD | TK-09 |  | BS VI HSD | TANK.TK-09.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VTF | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV RCL | MOV.DBBV-004.MAINTENANCE_STATUS | 0 | DBBV-004 | MOV IL1 |  |  |  |  | MOV.DBBV-006.MAINTENANCE_STATUS | 0 | DBBV-006 | MOV RCL | MOV.DBBV-005.MAINTENANCE_STATUS | 0 | DBBV-005 | MOV OL
1155 | Roorkee_M | TK-10_BS VI HSD | TK-10 |  | BS VI HSD | TANK.TK-10.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VTF | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV RCL | MOV.DBBV-007.MAINTENANCE_STATUS | 0 | DBBV-007 | MOV IL1 |  |  |  |  | MOV.DBBV-009.MAINTENANCE_STATUS | 0 | DBBV-009 | MOV RCL | MOV.DBBV-008.MAINTENANCE_STATUS | 0 | DBBV-008 | MOV OL
1155 | Roorkee_M | TK-11_BS VI MS | TK-11 |  | BS VI MS | TANK.TK-11.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VTF | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV RCL | MOV.DBBV-010.MAINTENANCE_STATUS | 0 | DBBV-010 | MOV IL1 |  |  |  |  | MOV.DBBV-012.MAINTENANCE_STATUS | 0 | DBBV-012 | MOV RCL | MOV.DBBV-011.MAINTENANCE_STATUS | 0 | DBBV-011 | MOV OL
1155 | Roorkee_M | TK-12_BS VI MS | TK-12 |  | BS VI MS | TANK.TK-12.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VTF | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV OL | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV RCL | MOV.DBBV-013.MAINTENANCE_STATUS | 0 | DBBV-013 | MOV IL1 |  |  |  |  | MOV.DBBV-015.MAINTENANCE_STATUS | 0 | DBBV-015 | MOV RCL | MOV.DBBV-014.MAINTENANCE_STATUS | 0 | DBBV-014 | MOV OL
1155 | Roorkee_M | TK-13_WATER | TK-13 |  | WATER | TANK.TK-13.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-14_WATER | TK-14 |  | WATER | TANK.TK-14.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-15_BS VI MS | TK-15 |  | BS VI MS | TANK.TK-15.MAINTENANCE_STATUS | 0
1155 | Roorkee_M | TK-16_BS VI MS | TK-16 |  | BS VI MS | TANK.TK-16.MAINTENANCE_STATUS | 0 | [21 empty] | 0
1155 | Roorkee_M | TK-17_BS VI HSD | TK-17 |  | BS VI HSD | TANK.TK-17.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VTF | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-18.MAINTENANCE_STATUS |  | ROSOV-18 | ROSOV RCL | MOV.DBBV-018.MAINTENANCE_STATUS | 0 | DBBV-018 | MOV IL1 |  |  |  |  | MOV.DBBV-020.MAINTENANCE_STATUS | 0 | DBBV-020 | MOV RCL | MOV.DBBV-019.MAINTENANCE_STATUS | 0 | DBBV-019 | MOV OL

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1155 | Roorkee | ADTV-PMP-01_POWERMS | ADTV-PMP-01 | POWERMS | Truck Loading |  | PUMP.ADTV-PMP-01.ON | 1 | PUMP.ADTV-PMP-01.OFF | 0 | PUMP.ADTV-PMP-01.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-01.MAINTENANCE_STATUS | 0
1155 | Roorkee | ADTV-PMP-02_POWERMS | ADTV-PMP-02 | POWERMS | Truck Loading |  | PUMP.ADTV-PMP-02.ON | 1 | PUMP.ADTV-PMP-02.OFF | 0 | PUMP.ADTV-PMP-02.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-02.MAINTENANCE_STATUS | 0
1155 | Roorkee | ADTV-PMP-03_TURBOHSD | ADTV-PMP-03 | TURBOHSD | Truck Loading |  | PUMP.ADTV-PMP-03.ON | 1 | PUMP.ADTV-PMP-03.OFF | 0 | PUMP.ADTV-PMP-03.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-03.MAINTENANCE_STATUS | 0
1155 | Roorkee | ADTV-PMP-04_TURBOHSD | ADTV-PMP-04 | TURBOHSD | Truck Loading |  | PUMP.ADTV-PMP-04.ON | 1 | PUMP.ADTV-PMP-04.OFF | 0 | PUMP.ADTV-PMP-04.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-04.MAINTENANCE_STATUS | 0
1155 | Roorkee | ADTV-PMP-05_BLUE DYE | ADTV-PMP-05 | BLUE DYE | Truck Loading |  | PUMP.ADTV-PMP-05.ON | 1 | PUMP.ADTV-PMP-05.OFF | 0 | PUMP.ADTV-PMP-05.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-05.MAINTENANCE_STATUS | 0
1155 | Roorkee | ADTV-PMP-06_BLUE DYE | ADTV-PMP-06 | BLUE DYE | Truck Loading |  | PUMP.ADTV-PMP-06.ON | 1 | PUMP.ADTV-PMP-06.OFF | 0 | PUMP.ADTV-PMP-06.REMOTE_STATUS | 0 | PUMP.ADTV-PMP-06.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-01_BS VI HSD | PMP-01 | BS VI HSD | Truck Loading |  | PUMP.PMP-01.ON | 1 | PUMP.PMP-01.OFF | 0 | PUMP.PMP-01.REMOTE_STATUS | 0 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-02_BS VI HSD | PMP-02 | BS VI HSD | Truck Loading |  | PUMP.PMP-02.ON | 1 | PUMP.PMP-02.OFF | 0 | PUMP.PMP-02.REMOTE_STATUS | 0 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-03_BS VI HSD | PMP-03 | BS VI HSD | Truck Loading |  | PUMP.PMP-03.ON | 1 | PUMP.PMP-03.OFF | 0 | PUMP.PMP-03.REMOTE_STATUS | 0 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-04_BS VI MS | PMP-04 | BS VI MS | Truck Loading |  | PUMP.PMP-04.ON | 1 | PUMP.PMP-04.OFF | 0 | PUMP.PMP-04.REMOTE_STATUS | 0 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-05_BS VI MS | PMP-05 | BS VI MS | Truck Loading |  | PUMP.PMP-05.ON | 1 | PUMP.PMP-05.OFF | 0 | PUMP.PMP-05.REMOTE_STATUS | 0 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-06_BS VI MS | PMP-06 | BS VI MS | Truck Loading |  | PUMP.PMP-06.ON | 1 | PUMP.PMP-06.OFF | 0 | PUMP.PMP-06.REMOTE_STATUS | 0 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-07_BS VI HSD | PMP-07 | BS VI HSD | Truck Loading |  | PUMP.PMP-07.ON | 1 | PUMP.PMP-07.OFF | 0 | PUMP.PMP-07.REMOTE_STATUS | 0 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-08_BS VI HSD | PMP-08 | BS VI HSD | Truck Loading |  | PUMP.PMP-08.ON | 1 | PUMP.PMP-08.OFF | 0 | PUMP.PMP-08.REMOTE_STATUS | 0 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-09_BS VI HSD | PMP-09 | BS VI HSD | Truck Loading |  | PUMP.PMP-09.ON | 1 | PUMP.PMP-09.OFF | 0 | PUMP.PMP-09.REMOTE_STATUS | 0 | PUMP.PMP-09.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-10_BS VI HSD | PMP-10 | BS VI HSD | Truck Loading |  | PUMP.PMP-10.ON | 1 | PUMP.PMP-10.OFF | 0 | PUMP.PMP-10.REMOTE_STATUS | 0 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-11_BS VI MS | PMP-11 | BS VI MS | Truck Loading |  | PUMP.PMP-11.ON | 1 | PUMP.PMP-11.OFF | 0 | PUMP.PMP-11.REMOTE_STATUS | 0 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-12_BS VI MS | PMP-12 | BS VI MS | Truck Loading |  | PUMP.PMP-12.ON | 1 | PUMP.PMP-12.OFF | 0 | PUMP.PMP-12.REMOTE_STATUS | 0 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-13_BS VI MS | PMP-13 | BS VI MS | Truck Loading |  | PUMP.PMP-13.ON | 1 | PUMP.PMP-13.OFF | 0 | PUMP.PMP-13.REMOTE_STATUS | 0 | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-14_BS VI MS | PMP-14 | BS VI MS | Truck Loading |  | PUMP.PMP-14.ON | 1 | PUMP.PMP-14.OFF | 0 | PUMP.PMP-14.REMOTE_STATUS | 0 | PUMP.PMP-14.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-15_BS VI HSD | PMP-15 | BS VI HSD | Truck Loading |  | PUMP.PMP-15.ON | 1 | PUMP.PMP-15.OFF | 0 | PUMP.PMP-15.REMOTE_STATUS | 0 | PUMP.PMP-15.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-16_BS VI HSD | PMP-16 | BS VI HSD | Truck Loading |  | PUMP.PMP-16.ON | 1 | PUMP.PMP-16.OFF | 0 | PUMP.PMP-16.REMOTE_STATUS | 0 | PUMP.PMP-16.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-17_ETHANOL | PMP-17 | ETHANOL | Truck Loading |  | PUMP.PMP-17.ON | 1 | PUMP.PMP-17.OFF | 0 | PUMP.PMP-17.REMOTE_STATUS | 0 | PUMP.PMP-17.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-18_ETHANOL | PMP-18 | ETHANOL | Truck Loading |  | PUMP.PMP-18.ON | 1 | PUMP.PMP-18.OFF | 0 | PUMP.PMP-18.REMOTE_STATUS | 0 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-19_BS VI HSD | PMP-19 | BS VI HSD | Wagon Loading |  | PUMP.PMP-19.ON | 1 | PUMP.PMP-19.OFF | 0 | PUMP.PMP-19.REMOTE_STATUS | 0 | PUMP.PMP-19.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-20_BS VI HSD | PMP-20 | BS VI HSD | Wagon Loading |  | PUMP.PMP-20.ON | 1 | PUMP.PMP-20.OFF | 0 | PUMP.PMP-20.REMOTE_STATUS | 0 | PUMP.PMP-20.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-21_BS IV HSD | PMP-21 | BS IV HSD | Wagon Loading |  | PUMP.PMP-21.ON | 1 | PUMP.PMP-21.OFF | 0 | PUMP.PMP-21.REMOTE_STATUS | 0 | PUMP.PMP-21.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-22_BS VI MS | PMP-22 | BS VI MS | Wagon Loading |  | PUMP.PMP-22.ON | 1 | PUMP.PMP-22.OFF | 0 | PUMP.PMP-22.REMOTE_STATUS | 0 | PUMP.PMP-22.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-23_BS VI MS | PMP-23 | BS VI MS | Wagon Loading |  | PUMP.PMP-23.ON | 1 | PUMP.PMP-23.OFF | 0 | PUMP.PMP-23.REMOTE_STATUS | 0 | PUMP.PMP-23.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-24_SKO | PMP-24 | SKO | Wagon Loading |  | PUMP.PMP-24.ON | 1 | PUMP.PMP-24.OFF | 0 | PUMP.PMP-24.REMOTE_STATUS | 0 | PUMP.PMP-24.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-25_SKO | PMP-25 | SKO | Wagon Loading |  | PUMP.PMP-25.ON | 1 | PUMP.PMP-25.OFF | 0 | PUMP.PMP-25.REMOTE_STATUS | 0 | PUMP.PMP-25.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-26_ETHANOL | PMP-26 | ETHANOL | Truck Loading |  | PUMP.PMP-26.ON | 1 | PUMP.PMP-26.OFF | 0 | PUMP.PMP-26.REMOTE_STATUS | 0 | PUMP.PMP-26.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-27_ETHANOL | PMP-27 | ETHANOL | Truck Loading |  | PUMP.PMP-27.ON | 1 | PUMP.PMP-27.OFF | 0 | PUMP.PMP-27.REMOTE_STATUS | 0 | PUMP.PMP-27.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-28_ETHANOL | PMP-28 | ETHANOL | Truck Loading |  | PUMP.PMP-28.ON | 1 | PUMP.PMP-28.OFF | 0 | PUMP.PMP-28.REMOTE_STATUS | 0 | PUMP.PMP-28.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-29_ETHANOL | PMP-29 | ETHANOL | Truck Loading |  | PUMP.PMP-29.ON | 1 | PUMP.PMP-29.OFF | 0 | PUMP.PMP-29.REMOTE_STATUS | 0 | PUMP.PMP-29.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-30_ETHANOL | PMP-30 | ETHANOL | Truck Loading |  | PUMP.PMP-30.ON | 1 | PUMP.PMP-30.OFF | 0 | PUMP.PMP-30.REMOTE_STATUS | 0 | PUMP.PMP-30.MAINTENANCE_STATUS | 0
1155 | Roorkee | PMP-IOCL-01_BS VI MS | PMP-IOCL-01 | BS VI MS | Truck Loading |  | PUMP.PMP-IOCL-01.ON | 1 | PUMP.PMP-IOCL-01.OFF | 0
1155 | Roorkee | PMP-IOCL-02_BS VI MS | PMP-IOCL-02 | BS VI MS | Truck Loading |  | PUMP.PMP-IOCL-02.ON | 1 | PUMP.PMP-IOCL-02.OFF | 0
1155 | Roorkee | PMP-IOCL-03_BS VI HSD | PMP-IOCL-03 | BS VI HSD | Truck Loading |  | PUMP.PMP-IOCL-03.ON | 1 | PUMP.PMP-IOCL-03.OFF | 0
1155 | Roorkee | PMP-IOCL-04_BS VI HSD | PMP-IOCL-04 | BS VI HSD | Truck Loading |  | PUMP.PMP-IOCL-04.ON | 1 | PUMP.PMP-IOCL-04.OFF | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP OFF STATUS | PUMP OFF STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | FIRE PUMP MAINTENANCE | FIRE PUMP MAINTENANCE Normal value | FIRE PUMP FAIL TO START 1 | FIRE PUMP FAIL TO START 1 Normal value | FIRE PUMP FAIL TO START 2 | FIRE PUMP FAIL TO START 2 Normal value | FIRE PUMP FAIL TO START 3 | FIRE PUMP FAIL TO START 3 Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP TRIPPED FAULT | FIRE PUMP TRIPPED FAULT Normal value | FIRE PUMP LLOP ALARM | FIRE PUMP LLOP ALARM Normal value | FIRE PUMP HWT ALARM | FIRE PUMP HWT ALARM Normal value
1155 | Roorkee | FWP-01_Water | FWP-01 | Water | PUMP HOUSE |  | PUMP.FWP-01.ON | 1 | PUMP.FWP-01.OFF | 0 | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_STANDBY1 | 0 |  |  |  |  | PUMP.FWP-01.PUMP_TRIPPED | 0 | PUMP.FWP-01.LOW_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1155 | Roorkee | FWP-02_Water | FWP-02 | Water | PUMP HOUSE |  | PUMP.FWP-02.ON | 1 | PUMP.FWP-02.OFF | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_STANDBY1 | 0 |  |  |  |  | PUMP.FWP-02.PUMP_TRIPPED | 0 | PUMP.FWP-02.LOW_OIL_PRESSURE_ALARM | 0 | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1155 | Roorkee | JCY-01_Jockey | JCY-01 | Jockey | PUMP HOUSE |  | PUMP.JCY-01.ON | 1 | PUMP.JCY-01.OFF | 0 | PUMP.JCY-01.REMOTE_STATUS | 0 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-01.PUMP_TRIPPED | 0
1155 | Roorkee | JCY-02_Jockey | JCY-02 | Jockey | PUMP HOUSE |  | PUMP.JCY-02.ON | 1 | PUMP.JCY-02.OFF | 0 | PUMP.JCY-02.REMOTE_STATUS | 0 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0 | PUMP.JCY-02.PUMP_TRIPPED | 0
1155 | Roorkee | Farthest Point PT_WATER Pressure_Near Tank no. 01 | Farthest Point PT | WATER Pressure | PT | Near Tank no. 01 | [6 empty] | PressureTransmitter.PT-01.MAINTENANCE_STATUS | 0
1155 | Roorkee | Nearest Point PT_WATER Pressure_FWP pump house | Nearest Point PT | WATER Pressure | PT | FWP pump house | [6 empty] | PressureTransmitter.PT-02.MAINTENANCE_STATUS | 0

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | UPS FAIL Normal Value | LOW BATTERY | LOW BATTERY Normal Value | UPS ON | UPS ON Normal Value | UPS MAIN AC FAIL | UPS MAIN AC FAIL Normal Value
1155 | Roorkee | UPS-01_CR - Process | UPS-01 | CR - Process | UPS.UPS-01.MAIN_AC_FAIL | 0 | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.UPS_ON | 0
1155 | Roorkee | UPS-02_CR - Process | UPS-02 | CR - Process | UPS.UPS-02.MAIN_AC_FAIL | 0 | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.UPS_ON | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | PLC A IS MASTER Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | PLC B IS MASTER Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | PLC A FAIL SAFE Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | PLC B FAIL SAFE Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | PLC A COOMUNCIATION Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | PLC B COOMUNCIATION Normal Value | Sensor_Id | Sensor_Type
1155 | Roorkee | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLC A | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLC B
1155 | Roorkee | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_FAIL_SAFE_STATUS | 0 | SFTPLC | PLC B | PLC.SFTPLC.PLCA_COMM_OK | 0 | SFTPLC | PLC A | PLC.SFTPLC.PLCB_COMM_OK | 0 | SFTPLC | PLC B

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | HCD 40 % ALARM Normal Value | HCD 20 % ALARM | HCD 20 % ALARM Normal Value | HCD FAULT | HCD FAULT Normal Value | MISALIGNMENT FAULT | MISALIGNMENT FAULT Normal Value | HCD MAINTENANCE | HCD MAINTENANCE Normal Value | HCD Hooter Activated | Normal value
1155 | Roorkee | HDS-01_HCD-OPENED-TYP1_TANKFARM TK11 12 MS | HDS-01 | HCD-OPENED-TYP1 | TANKFARM TK11 12 MS | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-02_HCD-OPENED-TYP2_TTL PUM HOUSE | HDS-02 | HCD-OPENED-TYP2 | TTL PUM HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-03_HCD-OPENED-TYP3_PLT PUMP HOUSE | HDS-03 | HCD-OPENED-TYP3 | PLT PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-04_HCD-FIXED-TYP1_TANKFARM TK-11 MS | HDS-04 | HCD-FIXED-TYP1 | TANKFARM TK-11 MS | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-07_HCD-FIXED-TYP4_TLF PUMP HOUSE | HDS-07 | HCD-FIXED-TYP4 | TLF PUMP HOUSE | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-08_HCD-OPEN-TYPE_NEAR TANK-8 | HDS-08 | HCD-OPEN-TYPE | NEAR TANK-8 | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HDS-09_HCD-FIXED-TYPE_NEAR TANK-8 | HDS-09 | HCD-FIXED-TYPE | NEAR TANK-8 | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | DYKE VALVE STATUS Normal Value | Dyke Hooter Activated | Normal value
1155 | Roorkee | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0
1155 | Roorkee | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | BARRIER GATE OPEN STATUS Normal value | BARRIER GATE CLOSE STATUS | BARRIER GATE CLOSE STATUS Normal value | BARRIER GATE LR STATUS | Normal value
1155 | Roorkee | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.CLOSE_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1155 | Roorkee | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.CLOSE_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | HOOTER STATUS Normal Value
1155 | Roorkee | HOOTER1_ANY_HOOTER_FOR_HCD_FIELD | HOOTER1 | ANY_HOOTER_FOR_HCD_FIELD | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1155 | Roorkee | HOOTER2_ACK_STATUS | HOOTER2 | ACK_STATUS | PLC.SFTPLC.HOOTER_ACK_STATUS | 0
1155 | Roorkee | HOOTER3_FIELD_1 | HOOTER3 | FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1155 | Roorkee | HOOTER4_FIELD_2 | HOOTER4 | FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1155 | Roorkee | HOOTER5_FIELD_3 | HOOTER5 | FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1155 | Roorkee | HOOTER6_FOR_ESD_CR | HOOTER6 | FOR_ESD_CR | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1155 | Roorkee | HOOTER7_FOR_HC_CR | HOOTER7 | FOR_HC_CR | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1155 | Roorkee | HOOTER8_FOR_RIMSEAL_CR | HOOTER8 | FOR_RIMSEAL_CR | PLC.SFTPLC.HOOTER_FOR_RIMSEAL_CR | 0
1155 | Roorkee | HOOTER9_RESET_STATUS | HOOTER9 | RESET_STATUS | PLC.SFTPLC.HOOTER_RESET_STATUS | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | ESD STATUS Normal Value | ESD MAINTENANCE STATUS | ESD MAINTENANCE STATUS Normal Value | All ROSOVs closed | All ROSOVs closed Normal value | Barrier Gate opened | Barrier Gate opened Normal Value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | All Tanks in Dormant Mode | All Tanks in Dormant Mode Normal value | All DBBVs Closed | All DBBVs Closed Normal value | ESD Command To Process PLC | ESD Command To Process PLC Normal value | Siren Activated | Siren Activated Normal value | ESD Hooter activated in control room | ESD Hooter activated in control room Normal value | Power ESD Activation after 120 Sec | Power ESD Activation after 120 Sec Normal value | TTL Dispatch in Dormant Mode | TTL Dispatch in Dormant Mode Normal value
1155 | Roorkee | ESD-01_INSIDE CONTROLROOM | ESD-01 | ESDPB-01 | INSIDE CONTROLROOM | ESD.ESD-01.ESD_STATUS | 0 | ESD.ESD-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-02_MCC ROOM | ESD-02 | ESDPB-02 | MCC ROOM | ESD.ESD-02.ESD_STATUS | 0 | ESD.ESD-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-03_SECURITY ROOM | ESD-03 | ESDPB-03 | SECURITY ROOM | ESD.ESD-03.ESD_STATUS | 0 | ESD.ESD-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-04_PLT PUMP HOUSE | ESD-04 | ESDPB-04 | PLT PUMP HOUSE | ESD.ESD-04.ESD_STATUS | 0 | ESD.ESD-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-05_LOCATION IN CHARGE ROOM | ESD-05 | ESDPB-05 | LOCATION IN CHARGE ROOM | ESD.ESD-05.ESD_STATUS | 0 | ESD.ESD-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-06_NEAR LUBE GODOWN - 1 | ESD-06 | ESDPB-06 | NEAR LUBE GODOWN - 1 | ESD.ESD-06.ESD_STATUS | 0 | ESD.ESD-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-07_NEAR FIRE WATER PUMP HOUSE | ESD-07 | ESDPB-07 | NEAR FIRE WATER PUMP HOUSE | ESD.ESD-07.ESD_STATUS | 0 | ESD.ESD-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-08_IN BETWEEN TK-08 AND TK-09 CATWALK SIDE | ESD-08 | ESDPB-08 | IN BETWEEN TK-08 AND TK-09 CATWALK SIDE | ESD.ESD-08.ESD_STATUS | 0 | ESD.ESD-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-09_NEAR TANK-10 CATWALK SIDE | ESD-09 | ESDPB-09 | NEAR TANK-10 CATWALK SIDE | ESD.ESD-09.ESD_STATUS | 0 | ESD.ESD-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-10_NEAR BULK AIR ELUMINATER | ESD-10 | ESDPB-10 | NEAR BULK AIR ELUMINATER | ESD.ESD-10.ESD_STATUS | 0 | ESD.ESD-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-11_TLF PUMP HOUSE | ESD-11 | ESDPB-11 | TLF PUMP HOUSE | ESD.ESD-11.ESD_STATUS | 0 | ESD.ESD-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-12_NEAR U/G TANK - 15/16 (BEHIND GANTRY) | ESD-12 | ESDPB-12 | NEAR U/G TANK - 15/16 (BEHIND GANTRY) | ESD.ESD-12.ESD_STATUS | 0 | ESD.ESD-12.MAINTENANCE_STATUS |  | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-13_IN BETWEEN TK-11 and TK-12 CATWALK SIDE | ESD-13 | ESDPB-13 | IN BETWEEN TK-11 and TK-12 CATWALK SIDE | ESD.ESD-13.ESD_STATUS | 0 | ESD.ESD-13.MAINTENANCE_STATUS |  | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-14_GANTRY CABIN | ESD-14 | ESDPB-14 | GANTRY CABIN | ESD.ESD-14.ESD_STATUS | 0 | ESD.ESD-14.MAINTENANCE_STATUS |  | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-15_GANTRY BAY 2 STAIRCASE | ESD-15 | ESDPB-15 | GANTRY BAY 2 STAIRCASE | ESD.ESD-15.ESD_STATUS | 0 | ESD.ESD-15.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-16_CENTRAL ESD | ESD-16 | ESD-SYSTEM | CENTRAL ESD | ESD.ESD-16.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-17_ESD DUE TO VIBRATING FORK | ESD-17 | ESD-VFT | ESD DUE TO VIBRATING FORK | ESD.ESD-17.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-18_ESD DUE TO RADAR RELAY | ESD-18 | ESD-RDR | ESD DUE TO RADAR RELAY | ESD.ESD-18.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-IOCL_ESD-IOCL | ESD-IOCL | ESD-IOCL | ESD-IOCL | ESD.ESD-IOCL.ESD_STATUS | 0 |  | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1155 | Roorkee | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | ESD-SOFT | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSE | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_TANKS_IN_DORMANT_EXCP_RECIEPT | 0 | PLC.SFTPLC.ALL_DBBV_CLOSED | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.EFFECT_POWER_ESD_ACTI | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | Sensor_Id | Sensor_Type | NO FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | NO FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | LOW FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | LOW FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | HIGH FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | HIGH FLOW STATUS OF BLEND | Normal value | Sensor_Id | Sensor_Type | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | METER OVERRUN STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BLEND OVERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BLEND UNDERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | ADD OVERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | ADD UNDERDOSE STATUS OF MAIN | Normal value | Sensor_Id | Sensor_Type | BCU LOADING STATUS | Normal value | Sensor_Id | Sensor_Type | K-FACTOR CHANGE STATUS | Normal value | Sensor_Id | Sensor_Type | K-FACTOR CHANGE STATUS BLEND | Normal value | Sensor_Id | Sensor_Type | BCU VS MFM TOTALIZER MISMATCH | Normal Value | Sensor_Id | Sensor_Type | DAY START TOTALIZER MISMATCH | Normal value | Sensor_Id | Sensor_Type | DAY START TOTALIZER MISMATCH BLEND | Normal value | Sensor_Id | Sensor_Type
1155 | Roorkee | LP 01_BC-501A_BS VI MS | LP 01 | TLF | BC-501A | BS VI MS | SmartLoad-Dual.BC-501A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-501A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-501A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-501A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-501A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-501A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 02_BC-501B_BS VI HSD | LP 02 | TLF | BC-501B | BS VI HSD | SmartLoad-Dual.BC-501B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-501B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-501B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-501B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-501B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-501B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 03_BC-502A_BS VI MS | LP 03 | TLF | BC-502A | BS VI MS | SmartLoad-Dual.BC-502A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-502A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-502A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-502A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-502A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-502A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 04_BC-502B_BS VI HSD | LP 04 | TLF | BC-502B | BS VI HSD | SmartLoad-Dual.BC-502B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-502B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-502B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-502B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-502B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-502B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 05_BC-503A_BS VI MS | LP 05 | TLF | BC-503A | BS VI MS | SmartLoad-Dual.BC-503A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-503A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-503A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-503A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-503A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-503A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 06_BC-503B_BS VI HSD | LP 06 | TLF | BC-503B | BS VI HSD | SmartLoad-Dual.BC-503B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-503B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-503B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-503B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-503B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-503B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-503B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-503B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 07_BC-504A_BS VI MS | LP 07 | TLF | BC-504A | BS VI MS | SmartLoad-Dual.BC-504A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-504A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-504A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-504A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-504A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-504A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 08_BC-504B_BS VI HSD | LP 08 | TLF | BC-504B | BS VI HSD | SmartLoad-Dual.BC-504B.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.NO_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-504B.LOW_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-504B.HIGH_FLOW_ALARM_STATUS_M3 | 0 | [6 empty] | SmartLoad-Dual.BC-504B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.METER_OVERRUN_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-504B.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-504B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 | [6 empty] | SmartLoad-Dual.BC-504B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-504B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1155 | Roorkee | LP 09_BC-505A_BS IV MS | LP 09 | TLF | BC-505A | BS IV MS | SmartLoad-Dual.BC-505A.EARTH_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.NO_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.LOW_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.HIGH_FLOW_ALARM_STATUS_M2 | 0 |  |  | SmartLoad-Dual.BC-505A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.METER_OVERRUN_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-505A.BLEND_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BLEND_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BATCH_STATUS |  |  |  | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-505A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 |  |  | SmartLoad-Dual.BC-505A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 |  |  | SmartLoad-Dual.BC-505A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1155 | Roorkee | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1155 | Roorkee | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1155 | Roorkee | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | TLF Gantry Permissive Power Off Normal value | All TLF Product Pumps Stopped | All TLF Product Pumps Stopped Normal value | TLF Header Line MOV Close | TLF Header Line MOV Close Normal value | Hooter activated in control room | Normal value
1155 | Roorkee | Two Fire Engine Running status | PLC.SFTPLC.CAUSE_ANY_FWP_IS_RUNNING | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR
1155 | Roorkee | WATER Level below Ref. Volume | PLC.SFTPLC.CAUSE_WATERTK_VOL_BELOW_90PCT | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR
1155 | Roorkee | Main Fire Engines not in REMOTE | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PLC.SFTPLC.TLF_GANTRY_PERMISSIVE_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0 | PLC.SFTPLC.EFFECT_HOOTER_FOR_DYKE_FWP_CR
1155 | Roorkee | Gantry Permissive Off |  |  | SmartLoad-Dual.BC-501A.PERMISSIVE_FROM_DNC_STATUS | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.EFFECT_ALL_HEADER_MOV_CLOSED | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | AIR COMPRESSOR FAULT STATUS Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1155 | Roorkee | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1155 | Roorkee | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.JCY-01.ON | 1 | PUMP.JCY-02.ON | 1 | PressureTransmitter.PT-02.PRESSURE |  | PressureTransmitter.PT-01.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.CAUSE_ANY_MAIN_FWP_IN_REMOTE_MANUAL | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1